## AnonDB - Copy
| Mod_ID | Confidential | Make | Model | Interconnect_Tech | Module_Area_(cm2) | Junction_Box_Type | Cell_Wafer_Type | Cell_Tech | Cell_Area_(cm2) | Total_Exposure | Nameplate_Isc_(A) | Nameplate_Voc_(V) | Nameplate_Imp_(A) | Nameplate Imp/Isc | Nameplate_Vmp_(V) | Nameplate Vmp/Voc | Nameplate_Pmp_(W) | Isc_(A) | Voc_(V) | Imp_(A) | Imp/Isc | Vmp_(V) | Vmp/Voc | Pmp_(W) | FF_(percent) | Measured_Temperature_(C) | Temp_Measurement_Method | Voltage_Temperature_Coefficient_(mV/C) | Simulator_Make | Simulator_Model | IV_Date | IV_Time | IV_Lab_Location | Camera_Make | Camera_Model | Detector_Type | Image_Resolution_(MP) | Longpass_Filter_Wavelength_(nm) | High_Applied_Current_(A) | High_Applied_Voltage_(V) | High_Sensor_Exposure_Time_(s) | Low_Applied_Current_(A) | Low_Applied_Voltage_(V) | Low_Sensor_Exposure_Time_(s) | ISO | Aperture | High_Temperature_(C) | Low_Temperature_(C) | Working_Distance_(m) | High_EL_Date | High_EL_Time | Low_EL_Date | Low_EL_Time | EL_Lab_Location | ELHPath | ELLPath | IVPath | Ref | Exposure_Step | Total_Exposure_Steps | RefIVPath | RefA | RefRefA | Ref_IV_Date | Ref_IV_Time | Current difference real/name | Voltage difference real/name
0 | 3903 |  | 35 | 1 |  | 16222.6 |  | mono-Si module |  |  | OE 640 days | 9.18 | 38.4 | 8.7 | 0.94771 | 31 | 0.80729 | 270 | 8.876 | 38.25 | 8.359 | 0.94175 | 30.78 | 0.80471 | 257.3 | 75.8 | 25.2 | back of panel |  | SPIRE | 4600SLP | 1/24/2020 | 9:55 | PSEL | FLI Proline |  |  |  |  | 7.094 | 40.378 | 25.6 | 1.78 | 35.95 | 153.6 |  |  |  |  | 2.36 | 1/27/2020 |  | 1/27/2020 |  | PSEL | ./EL/3903_35_1_01272020_80.tiff | ./EL/3903_35_1_01272020_20.tiff | ./IV/3903_35_1_01242020.csv | 0 | 0 | 1 | ./RefIV/3903_35_1_01242020.csv | 8.862 | 8.862 | 4/24/2018 | 10:46 | 0.99371 | 0.9968
1 | 3887 |  | 35 | 1 |  | 16222.6 |  | mono-Si module |  |  | OE 640 days | 9.18 | 38.4 | 8.7 | 0.94771 | 31 | 0.80729 | 270 | 8.836 | 38.2 | 8.331 | 0.94285 | 30.76 | 0.80524 | 256.2 | 75.9 | 25 | back of panel |  | SPIRE | 4600SLP | 1/24/2020 | 10:12 | PSEL | FLI Proline |  |  |  |  | 7.094 | 40.078 | 25.6 | 1.775 | 35.762 | 153.6 |  |  |  |  | 2.36 | 1/27/2020 |  | 1/27/2020 |  | PSEL | ./EL/3887_35_1_01272020_80.tiff | ./EL/3887_35_1_01272020_20.tiff | ./IV/3887_35_1_01242020.csv | 0 | 0 | 2 | ./RefIV/3887_35_1_01242020.csv | 8.862 | 8.862 | 4/24/2018 | 8:25 | 0.99487 | 0.99745
2 | 3887 |  | 35 | 1 |  | 16222.6 |  | mono-Si module |  |  | OE 1024 days | 9.18 | 38.4 | 8.7 | 0.94771 | 31 | 0.80729 | 270 | 8.829 | 38.19 | 8.308 | 0.94099 | 30.58 | 0.80073 | 254.1 | 75.3 | 25.4 | back of panel |  | SPIRE | 4600SLP | 2021-11-02 | 13:48 | PSEL | FLI Proline |  |  |  |  | 7.1 | 40.1 | 25.6 | 1.8 | 35.9 | 153.6 |  |  |  |  | 2.36 | 2/22/2021 |  | 2/22/2021 |  | PSEL | ./EL/3887_35_1_02222021_80.tiff | ./EL/3887_35_1_02222021_20.tiff | ./IV/3887_35_1_02112021.csv | 0 | 1 | 2 | ./RefIV/3887_35_1_02112021.csv | 8.862 | 8.862 | 4/24/2018 | 8:25 | 0.99291 | 0.99188
3 | 3899 |  | 35 | 1 |  | 16222.6 |  | mono-Si module |  |  | OE 640 days | 9.18 | 38.4 | 8.7 | 0.94771 | 31 | 0.80729 | 270 | 8.835 | 38.22 | 8.371 | 0.94748 | 30.78 | 0.80534 | 257.6 | 76.3 | 25.3 | back of panel |  | SPIRE | 4600SLP | 1/24/2020 | 10:03 | PSEL | FLI Proline |  |  |  |  | 7.094 | 40.078 | 25.6 | 1.775 | 35.762 | 153.6 |  |  |  |  | 2.36 | 1/27/2020 |  | 1/27/2020 |  | PSEL | ./EL/3899_35_1_01272020_80.tiff | ./EL/3899_35_1_01272020_20.tiff | ./IV/3899_35_1_01242020.csv | 0 | 0 | 2 | ./RefIV/3899_35_1_01242020.csv | 8.862 | 8.862 | 4/24/2018 | 10:23 | 0.99976 | 0.99758
4 | 3899 |  | 35 | 1 |  | 16222.6 |  | mono-Si module |  |  | OE 1024 days | 9.18 | 38.4 | 8.7 | 0.94771 | 31 | 0.80729 | 270 | 8.818 | 38.23 | 8.338 | 0.94557 | 30.57 | 0.79963 | 254.9 | 75.6 | 25.4 | back of panel |  | SPIRE | 4600SLP | 2021-11-02 | 13:37 | PSEL | FLI Proline |  |  |  |  | 7.1 | 40.2 | 25.6 | 1.8 | 36 | 153.6 |  |  |  |  | 2.36 | 2/22/2021 |  | 2/22/2021 |  | PSEL | ./EL/3899_35_1_02222021_80.tiff | ./EL/3899_35_1_02222021_20.tiff | ./IV/3899_35_1_02112021.csv | 0 | 1 | 2 | ./RefIV/3899_35_1_02112021.csv | 8.862 | 8.862 | 4/24/2018 | 10:23 | 0.99774 | 0.99051
5 | 3883 |  | 35 | 1 |  | 16222.6 |  | mono-Si module |  |  | OE 640 days | 9.18 | 38.4 | 8.7 | 0.94771 | 31 | 0.80729 | 270 | 8.84 | 38.2 | 8.344 | 0.94389 | 30.7 | 0.80366 | 256.2 | 75.9 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/24/2020 | 10:04 | PSEL | FLI Proline |  |  |  |  | 7.094 | 40.228 | 25.6 | 1.78 | 35.874 | 153.6 |  |  |  |  | 2.36 | 1/27/2020 |  | 1/27/2020 |  | PSEL | ./EL/3883_35_1_01272020_80.tiff | ./EL/3883_35_1_01272020_20.tiff | ./IV/3883_35_1_01242020.csv | 0 | 0 | 1 | ./RefIV/3883_35_1_01242020.csv | 8.862 | 8.862 | 4/24/2018 | 7:55 | 0.99597 | 0.99551
6 | 10085 |  | 35 | 1 |  | 16222.6 |  | mono-Si module |  |  | OE 640 days | 9.18 | 38.4 | 8.7 | 0.94771 | 31 | 0.80729 | 270 | 8.866 | 37.93 | 8.399 | 0.94733 | 30.47 | 0.80332 | 255.9 | 76.1 | 25.2 | back of panel |  | SPIRE | 4600SLP | 1/24/2020 | 9:44 | PSEL | FLI Proline |  |  |  |  | 7.094 | 39.515 | 25.6 | 1.78 | 35.274 | 153.6 |  |  |  |  | 2.36 | 1/27/2020 |  | 1/27/2020 |  | PSEL | ./EL/10085_35_1_01272020_80.tiff | ./EL/10085_35_1_01272020_20.tiff | ./IV/10085_35_1_01242020.csv | 0 | 0 | 2 | ./RefIV/10085_35_1_01242020.csv | 8.862 | 8.862 | 4/24/2018 | 7:29 | 0.99959 | 0.99508
7 | 10085 |  | 35 | 1 |  | 16222.6 |  | mono-Si module |  |  | OE 1024 days | 9.18 | 38.4 | 8.7 | 0.94771 | 31 | 0.80729 | 270 | 8.839 | 37.98 | 8.38 | 0.94807 | 30.44 | 0.80147 | 255.1 | 76 | 25 | back of panel |  | SPIRE | 4600SLP | 2021-11-02 | 13:21 | PSEL | FLI Proline |  |  |  |  | 7.1 | 39.6 | 25.6 | 1.8 | 35.5 | 153.6 |  |  |  |  | 2.36 | 2/22/2021 |  | 2/22/2021 |  | PSEL | ./EL/10085_35_1_02222021_80.tiff | ./EL/10085_35_1_02222021_20.tiff | ./IV/10085_35_1_02112021.csv | 0 | 1 | 2 | ./RefIV/10085_35_1_02112021.csv | 8.862 | 8.862 | 4/24/2018 | 7:29 | 1.0004 | 0.99279
8 | 3895 |  | 35 | 1 |  | 16222.6 |  | mono-Si module |  |  | OE 640 days | 9.18 | 38.4 | 8.7 | 0.94771 | 31 | 0.80729 | 270 | 8.864 | 38.19 | 8.358 | 0.94292 | 30.64 | 0.8023 | 256.1 | 75.7 | 25.3 | back of panel |  | SPIRE | 4600SLP | 1/24/2020 | 9:58 | PSEL | FLI Proline |  |  |  |  | 7.094 | 40.303 | 25.6 | 1.785 | 35.978 | 153.6 |  |  |  |  | 2.36 | 1/27/2020 |  | 1/27/2020 |  | PSEL | ./EL/3895_35_1_01272020_80.tiff | ./EL/3895_35_1_01272020_20.tiff | ./IV/3895_35_1_01242020.csv | 0 | 0 | 1 | ./RefIV/3895_35_1_01242020.csv | 8.862 | 8.862 | 4/24/2018 | 9:51 | 0.99494 | 0.99382
9 | 3905 |  | 35 | 1 |  | 16222.6 |  | mono-Si module |  |  | OE 640 days | 9.18 | 38.4 | 8.7 | 0.94771 | 31 | 0.80729 | 270 | 8.882 | 38.18 | 8.42 | 0.94798 | 30.71 | 0.80435 | 258.6 | 76.2 | 25.3 | back of panel |  | SPIRE | 4600SLP | 1/24/2020 | 9:50 | PSEL | FLI Proline |  |  |  |  | 7.094 | 40.378 | 25.6 | 1.78 | 36.062 | 1536 |  |  |  |  | 2.36 | 1/27/2020 |  | 1/27/2020 |  | PSEL | ./EL/3905_35_1_01272020_80.tiff | ./EL/3905_35_1_01272020_20.tiff | ./IV/3905_35_1_01242020.csv | 0 | 0 | 3 | ./RefIV/3905_35_1_01242020.csv | 8.862 | 8.862 | 4/24/2018 | 10:58 | 1.0003 | 0.99635
10 | 3905 |  | 35 | 1 |  | 16222.6 |  | mono-Si module |  |  | OE 1024 days | 9.18 | 38.4 | 8.7 | 0.94771 | 31 | 0.80729 | 270 | 8.851 | 38.26 | 8.395 | 0.94848 | 30.69 | 0.80214 | 257.6 | 76.1 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2021-11-02 | 13:26 | PSEL | FLI Proline |  |  |  |  | 7.1 | 40.1 | 25.6 | 1.8 | 35.9 | 153.6 |  |  |  |  | 2.36 | 2/22/2021 |  | 2/22/2021 |  | PSEL | ./EL/3905_35_1_02222021_80.tiff | ./EL/3905_35_1_02222021_20.tiff | ./IV/3905_35_1_02112021.csv | 0 | 1 | 3 | ./RefIV/3905_35_1_02112021.csv | 8.862 | 8.862 | 4/24/2018 | 10:58 | 1.0008 | 0.99362
11 | 3889 |  | 35 | 1 |  | 16222.6 |  | mono-Si module |  |  | OE 640 days | 9.18 | 38.4 | 8.7 | 0.94771 | 31 | 0.80729 | 270 | 8.846 | 38.17 | 8.347 | 0.94359 | 30.41 | 0.7967 | 253.8 | 75.2 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/24/2020 | 10:16 | PSEL | FLI Proline |  |  |  |  | 7.094 | 40.153 | 25.6 | 1.775 | 35.612 | 153.9 |  |  |  |  | 2.36 | 1/27/2020 |  | 1/27/2020 |  | PSEL | ./EL/3889_35_1_01272020_80.tiff | ./EL/3889_35_1_01272020_20.tiff | ./IV/3889_35_1_01242020.csv | 0 | 0 | 1 | ./RefIV/3889_35_1_01242020.csv | 8.862 | 8.862 | 4/24/2018 | 8:46 | 0.99565 | 0.98688
12 | 3886 |  | 35 | 1 |  | 16222.6 |  | mono-Si module |  |  | OE 640 days | 9.18 | 38.4 | 8.7 | 0.94771 | 31 | 0.80729 | 270 | 8.841 | 38.19 | 8.348 | 0.94424 | 30.73 | 0.80466 | 256.5 | 76 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/24/2020 | 10:10 | PSEL | FLI Proline |  |  |  |  | 7.094 | 40.266 | 25.6 | 1.78 | 35.95 | 153.6 |  |  |  |  | 2.36 | 1/27/2020 |  | 1/27/2020 |  | PSEL | ./EL/3886_35_1_01272020_80.tiff | ./EL/3886_35_1_01272020_20.tiff | ./IV/3886_35_1_01242020.csv | 0 | 0 | 2 | ./RefIV/3886_35_1_01242020.csv | 8.862 | 8.862 | 4/24/2018 | 8:18 | 0.99633 | 0.99674
13 | 3886 |  | 35 | 1 |  | 16222.6 |  | mono-Si module |  |  | OE 1024 days | 9.18 | 38.4 | 8.7 | 0.94771 | 31 | 0.80729 | 270 | 8.832 | 38.25 | 8.32 | 0.94203 | 30.59 | 0.79974 | 254.5 | 75.3 | 24.6 | back of panel |  | SPIRE | 4600SLP | 2021-11-02 | 13:58 | PSEL | FLI Proline |  |  |  |  | 7.1 | 40.2 | 25.6 | 1.8 | 35.9 | 153.6 |  |  |  |  | 2.36 | 2/22/2021 |  | 2/22/2021 |  | PSEL | ./EL/3886_35_1_02222021_80.tiff | ./EL/3886_35_1_02222021_20.tiff | ./IV/3886_35_1_02112021.csv | 0 | 1 | 2 | ./RefIV/3886_35_1_02112021.csv | 8.862 | 8.862 | 4/24/2018 | 8:18 | 0.994 | 0.99064
14 | 3884 |  | 35 | 1 |  | 16222.6 |  | mono-Si module |  |  | OE 640 days | 9.18 | 38.4 | 8.7 | 0.94771 | 31 | 0.80729 | 270 | 8.847 | 38.13 | 8.337 | 0.94235 | 30.67 | 0.80435 | 255.7 | 75.8 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/24/2020 | 10:08 | PSEL | FLI Proline |  |  |  |  | 7.094 | 40.191 | 25.6 | 1.78 | 35.874 | 93.6 |  |  |  |  | 2.36 | 1/27/2020 |  | 1/27/2020 |  | PSEL | ./EL/3884_35_1_01272020_80.tiff | ./EL/3884_35_1_01272020_20.tiff | ./IV/3884_35_1_01242020.csv | 0 | 0 | 2 | ./RefIV/3884_35_1_01242020.csv | 8.862 | 8.862 | 4/24/2018 | 8:02 | 0.99435 | 0.99636
15 | 3884 |  | 35 | 1 |  | 16222.6 |  | mono-Si module |  |  | OE 1024 days | 9.18 | 38.4 | 8.7 | 0.94771 | 31 | 0.80729 | 270 | 8.841 | 38.19 | 8.318 | 0.94084 | 30.57 | 0.80047 | 254.3 | 75.3 | 24.7 | back of panel |  | SPIRE | 4600SLP | 2021-11-02 | 13:54 | PSEL | FLI Proline |  |  |  |  | 7.1 | 40.1 | 25.6 | 1.8 | 35.9 | 153.6 |  |  |  |  | 2.36 | 2/22/2021 |  | 2/22/2021 |  | PSEL | ./EL/3884_35_1_02222021_80.tiff | ./EL/3884_35_1_02222021_20.tiff | ./IV/3884_35_1_02112021.csv | 0 | 1 | 2 | ./RefIV/3884_35_1_02112021.csv | 8.862 | 8.862 | 4/24/2018 | 8:02 | 0.99275 | 0.99155
16 | 10084 |  | 35 | 1 |  | 16222.6 |  | mono-Si module |  |  | OE 640 days | 9.18 | 38.4 | 8.7 | 0.94771 | 31 | 0.80729 | 270 | 8.859 | 37.9 | 8.382 | 0.94616 | 30.58 | 0.80686 | 256.3 | 76.3 | 25.3 | back of panel |  | SPIRE | 4600SLP | 1/24/2020 | 9:39 | PSEL | FLI Proline |  |  |  |  | 7.094 | 39.44 | 25.6 | 1.78 | 35.274 | 1536 |  |  |  |  | 2.36 | 1/27/2020 |  | 1/27/2020 |  | PSEL | ./EL/10084_35_1_01272020_80.tiff | ./EL/10084_35_1_01272020_20.tiff | ./IV/10084_35_1_01242020.csv | 0 | 0 | 2 | ./RefIV/10084_35_1_01242020.csv | 8.862 | 8.862 | 4/24/2018 | 7:37 | 0.99836 | 0.99947
17 | 10084 |  | 35 | 1 |  | 16222.6 |  | mono-Si module |  |  | OE 1024 days | 9.18 | 38.4 | 8.7 | 0.94771 | 31 | 0.80729 | 270 | 8.844 | 37.99 | 8.365 | 0.94584 | 30.61 | 0.80574 | 256 | 76.2 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-11-02 | 13:19 | PSEL | FLI Proline |  |  |  |  | 7.1 | 39.5 | 25.6 | 1.8 | 35.4 | 153.6 |  |  |  |  | 2.36 | 2/22/2021 |  | 2/22/2021 |  | PSEL | ./EL/10084_35_1_02222021_80.tiff | ./EL/10084_35_1_02222021_20.tiff | ./IV/10084_35_1_02112021.csv | 0 | 1 | 2 | ./RefIV/10084_35_1_02112021.csv | 8.862 | 8.862 | 4/24/2018 | 7:37 | 0.99802 | 0.99808
18 | 3904 |  | 35 | 1 |  | 16222.6 |  | mono-Si module |  |  | OE 640 days | 9.18 | 38.4 | 8.7 | 0.94771 | 31 | 0.80729 | 270 | 8.861 | 38.27 | 8.354 | 0.94278 | 30.67 | 0.80141 | 256.2 | 75.6 | 25.2 | back of panel |  | SPIRE | 4600SLP | 1/24/2020 | 9:52 | PSEL | FLI Proline |  |  |  |  | 7.094 | 40.416 | 25.6 | 1.775 | 36.062 | 153.6 |  |  |  |  | 2.36 | 1/27/2020 |  | 1/27/2020 |  | PSEL | ./EL/3904_35_1_01272020_80.tiff | ./EL/3904_35_1_01272020_20.tiff | ./IV/3904_35_1_01242020.csv | 0 | 0 | 1 | ./RefIV/3904_35_1_01242020.csv | 8.862 | 8.862 | 4/24/2018 | 10:52 | 0.9948 | 0.99272
19 | 3891 |  | 35 | 1 |  | 16222.6 |  | mono-Si module |  |  | OE 640 days | 9.18 | 38.4 | 8.7 | 0.94771 | 31 | 0.80729 | 270 | 8.839 | 38.21 | 8.347 | 0.94434 | 30.71 | 0.80372 | 256.4 | 75.9 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/24/2020 | 10:14 | PSEL | FLI Proline |  |  |  |  | 7.094 | 40.153 | 25.6 | 1.785 | 35.974 | 153.6 |  |  |  |  | 2.36 | 1/27/2020 |  | 1/27/2020 |  | PSEL | ./EL/3891_35_1_01272020_80.tiff | ./EL/3891_35_1_01272020_20.tiff | ./IV/3891_35_1_01242020.csv | 0 | 0 | 2 | ./RefIV/3891_35_1_01242020.csv | 8.862 | 8.862 | 4/24/2018 | 9:02 | 0.99644 | 0.99557
20 | 3891 |  | 35 | 1 |  | 16222.6 |  | mono-Si module |  |  | OE 1024 days | 9.18 | 38.4 | 8.7 | 0.94771 | 31 | 0.80729 | 270 | 8.826 | 38.26 | 8.328 | 0.94358 | 30.65 | 0.8011 | 255.2 | 75.6 | 24.8 | back of panel |  | SPIRE | 4600SLP | 2021-11-02 | 13:52 | PSEL | FLI Proline |  |  |  |  | 7.1 | 37.5 | 25.6 | 1.8 | 36.1 | 153.6 |  |  |  |  | 2.36 | 2/22/2021 |  | 2/22/2021 |  | PSEL | ./EL/3891_35_1_02222021_80.tiff | ./EL/3891_35_1_02222021_20.tiff | ./IV/3891_35_1_02112021.csv | 0 | 1 | 2 | ./RefIV/3891_35_1_02112021.csv | 8.862 | 8.862 | 4/24/2018 | 9:02 | 0.99564 | 0.99233
21 | 3894 |  | 35 | 1 |  | 16222.6 |  | mono-Si module |  |  | OE 640 days | 9.18 | 38.4 | 8.7 | 0.94771 | 31 | 0.80729 | 270 | 8.843 | 38.27 | 8.344 | 0.94357 | 30.88 | 0.8069 | 257.7 | 76.1 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/24/2020 | 10:01 | PSEL | FLI Proline |  |  |  |  | 7.094 | 40.341 | 25.6 | 1.775 | 36.1 | 153.6 |  |  |  |  | 2.36 | 1/27/2020 |  | 1/27/2020 |  | PSEL | ./EL/3894_35_1_01272020_80.tiff | ./EL/3894_35_1_01272020_20.tiff | ./IV/3894_35_1_01242020.csv | 0 | 0 | 1 | ./RefIV/3894_35_1_01242020.csv | 8.862 | 8.862 | 4/24/2018 | 9:46 | 0.99563 | 0.99951
22 | 3902 |  | 35 | 1 |  | 16222.6 |  | mono-Si module |  |  | OE 640 days | 9.18 | 38.4 | 8.7 | 0.94771 | 31 | 0.80729 | 270 | 8.868 | 38.22 | 8.36 | 0.94272 | 30.64 | 0.80167 | 256.1 | 75.6 | 25.2 | back of panel |  | SPIRE | 4600SLP | 1/24/2020 | 9:57 | PSEL | FLI Proline |  |  |  |  | 7.094 | 40.228 | 25.6 | 1.78 | 35.912 | 153.6 |  |  |  |  | 2.36 | 1/27/2020 |  | 1/27/2020 |  | PSEL | ./EL/3902_35_1_01272020_80.tiff | ./EL/3902_35_1_01272020_20.tiff | ./IV/3902_35_1_01242020.csv | 0 | 0 | 1 | ./RefIV/3902_35_1_01242020.csv | 8.862 | 8.862 | 4/24/2018 | 10:38 | 0.99473 | 0.99304
23 | 3898 |  | 35 | 1 |  | 16222.6 |  | mono-Si module |  |  | OE 1024 days | 9.18 | 38.4 | 8.7 | 0.94771 | 31 | 0.80729 | 270 | 8.855 | 38.17 | 8.322 | 0.93981 | 30.54 | 0.8001 | 254.2 | 75.2 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-11-02 | 13:36 | PSEL | FLI Proline |  |  |  |  | 7.1 | 40.1 | 25.6 | 1.8 | 35.9 | 153.6 |  |  |  |  | 2.36 | 2/22/2021 |  | 2/22/2021 |  | PSEL | ./EL/3898_35_1_02222021_80.tiff | ./EL/3898_35_1_02222021_20.tiff | ./IV/3898_35_1_02112021.csv | 0 | 0 | 1 | ./RefIV/3898_35_1_02112021.csv | 8.862 | 8.862 | 4/24/2018 | 10:15 | 0.99166 | 0.9911
24 | 3907 |  | 35 | 1 |  | 16222.6 |  | mono-Si module |  |  | OE 1024 days | 9.18 | 38.4 | 8.7 | 0.94771 | 31 | 0.80729 | 270 | 8.85 | 38.27 | 8.325 | 0.94068 | 30.63 | 0.80037 | 255 | 75.3 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-11-02 | 13:41 | PSEL | FLI Proline |  |  |  |  | 7.1 | 40.1 | 25.6 | 1.8 | 35.9 | 153.6 |  |  |  |  | 2.36 | 2/22/2021 |  | 2/22/2021 |  | PSEL | ./EL/3907_35_1_02222021_80.tiff | ./EL/3907_35_1_02222021_20.tiff | ./IV/3907_35_1_02112021.csv | 0 | 0 | 1 | ./RefIV/3907_35_1_02112021.csv | 8.862 | 8.862 | 4/24/2018 | 11:10 | 0.99258 | 0.99142
25 | 3885 |  | 35 | 1 |  | 16222.6 |  | mono-Si module |  |  | OE 1024 days | 9.18 | 38.4 | 8.7 | 0.94771 | 31 | 0.80729 | 270 | 8.819 | 38.22 | 8.326 | 0.9441 | 30.52 | 0.79853 | 254.1 | 75.4 | 24.8 | back of panel |  | SPIRE | 4600SLP | 2021-11-02 | 13:55 | PSEL | FLI Proline |  |  |  |  | 7.1 | 40.2 | 25.6 | 1.8 | 36 | 153.6 |  |  |  |  | 2.36 | 2/22/2021 |  | 2/22/2021 |  | PSEL | ./EL/3885_35_1_02222021_80.tiff | ./EL/3885_35_1_02222021_20.tiff | ./IV/3885_35_1_02112021.csv | 0 | 0 | 1 | ./RefIV/3885_35_1_02112021.csv | 8.862 | 8.862 | 4/24/2018 | 8:08 | 0.99619 | 0.98915
26 | 3893 |  | 35 | 1 |  | 16222.6 |  | mono-Si module |  |  | OE 1024 days | 9.18 | 38.4 | 8.7 | 0.94771 | 31 | 0.80729 | 270 | 8.844 | 38.26 | 8.334 | 0.94233 | 30.51 | 0.79744 | 254.3 | 75.2 | 25.3 | back of panel |  | SPIRE | 4600SLP | 2021-11-02 | 13:44 | PSEL | FLI Proline |  |  |  |  | 7.1 | 40.2 | 25.6 | 1.8 | 35.9 | 153.6 |  |  |  |  | 2.36 | 2/22/2021 |  | 2/22/2021 |  | PSEL | ./EL/3893_35_1_02222021_80.tiff | ./EL/3893_35_1_02222021_20.tiff | ./IV/3893_35_1_02112021.csv | 0 | 0 | 1 | ./RefIV/3893_35_1_02112021.csv | 8.862 | 8.862 | 4/24/2018 | 9:37 | 0.99432 | 0.98779
27 | 4482 |  | 7 | 1 |  | 16255.6 |  | multi-Si module |  |  | OE 0 days | 8.84 | 38.09 | 8.26 | 0.93439 | 31.48 | 0.82646 | 260 | 9.103 | 37.89 | 8.639 | 0.94903 | 30.63 | 0.80839 | 264.6 | 76.7 | 25.3 | back of panel |  | SPIRE | 4600SLP | 1/20/2020 | 7:28 | PSEL | FLI Proline |  |  |  |  | 7.293 | 39.59 | 51.2 | 1.825 | 35.424 | 204.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/4482_7_1_01172020_80.tiff | ./EL/4482_7_1_01172020_20.tiff | ./IV/4482_7_1_01202020.csv | 0 | 0 | 1 | ./RefIV/4482_7_1_01202020.csv | 8.862 | 8.862 | 1/20/2020 | 7:28 | 1.0157 | 0.97813
28 | 4481 |  | 7 | 1 |  | 16255.6 |  | multi-Si module |  |  | OE 0 days | 8.84 | 38.09 | 8.26 | 0.93439 | 31.48 | 0.82646 | 260 | 9.087 | 37.95 | 8.638 | 0.95059 | 30.71 | 0.80922 | 265.3 | 76.9 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/20/2020 | 7:26 | PSEL | FLI Proline |  |  |  |  | 7.278 | 39.553 | 51.2 | 1.815 | 35.462 | 204.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/4481_7_1_01172020_80.tiff | ./EL/4481_7_1_01172020_20.tiff | ./IV/4481_7_1_01202020.csv | 0 | 0 | 1 | ./RefIV/4481_7_1_01202020.csv | 8.862 | 8.862 | 1/20/2020 | 7:26 | 1.0173 | 0.97914
29 | 4477 |  | 7 | 1 |  | 16255.6 |  | multi-Si module |  |  | OE 0 days | 8.84 | 38.09 | 8.26 | 0.93439 | 31.48 | 0.82646 | 260 | 9.101 | 37.97 | 8.652 | 0.95066 | 30.7 | 0.80853 | 265.6 | 76.9 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/20/2020 | 7:17 | PSEL | FLI Proline |  |  |  |  | 7.283 | 39.628 | 51.2 | 1.82 | 35.537 | 204.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/4477_7_1_01172020_80.tiff | ./EL/4477_7_1_01172020_20.tiff | ./IV/4477_7_1_01202020.csv | 0 | 0 | 1 | ./RefIV/4477_7_1_01202020.csv | 8.862 | 8.862 | 1/20/2020 | 7:17 | 1.0174 | 0.9783
30 | 4474 |  | 7 | 1 |  | 16255.6 |  | multi-Si module |  |  | OE 0 days | 8.84 | 38.09 | 8.26 | 0.93439 | 31.48 | 0.82646 | 260 | 9.059 | 37.83 | 8.605 | 0.94988 | 30.56 | 0.80782 | 262.9 | 76.7 | 25.2 | back of panel |  | SPIRE | 4600SLP | 1/20/2020 | 7:03 | PSEL | FLI Proline |  |  |  |  | 7.253 | 38.839 | 51.2 | 1.815 | 35.974 | 204.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/4474_7_1_01172020_80.tiff | ./EL/4474_7_1_01172020_20.tiff | ./IV/4474_7_1_01202020.csv | 0 | 0 | 1 | ./RefIV/4474_7_1_01202020.csv | 8.862 | 8.862 | 1/20/2020 | 7:03 | 1.0166 | 0.97745
31 | 4478 |  | 7 | 1 |  | 16255.6 |  | multi-Si module |  |  | OE 0 days | 8.84 | 38.09 | 8.26 | 0.93439 | 31.48 | 0.82646 | 260 | 9.082 | 37.91 | 8.642 | 0.95155 | 30.65 | 0.80849 | 264.9 | 76.9 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/20/2020 | 7:19 | PSEL | FLI Proline |  |  |  |  | 7.278 | 39.628 | 51.2 | 1.82 | 35.424 | 204.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/4478_7_1_01172020_80.tiff | ./EL/4478_7_1_01172020_20.tiff | ./IV/4478_7_1_01202020.csv | 0 | 0 | 1 | ./RefIV/4478_7_1_01202020.csv | 8.862 | 8.862 | 1/20/2020 | 7:19 | 1.0184 | 0.97826
32 | 4476 |  | 7 | 1 |  | 16255.6 |  | multi-Si module |  |  | OE 0 days | 8.84 | 38.09 | 8.26 | 0.93439 | 31.48 | 0.82646 | 260 | 9.108 | 37.9 | 8.612 | 0.94554 | 30.56 | 0.80633 | 263.2 | 76.2 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/20/2020 | 7:12 | PSEL | FLI Proline |  |  |  |  | 7.298 | 39.44 | 51.2 | 1.82 | 35.424 | 204.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/4476_7_1_01172020_80.tiff | ./EL/4476_7_1_01172020_20.tiff | ./IV/4476_7_1_01202020.csv | 0 | 0 | 1 | ./RefIV/4476_7_1_01202020.csv | 8.862 | 8.862 | 1/20/2020 | 7:12 | 1.0119 | 0.97564
33 | 4479 |  | 7 | 1 |  | 16255.6 |  | multi-Si module |  |  | OE 0 days | 8.84 | 38.09 | 8.26 | 0.93439 | 31.48 | 0.82646 | 260 | 9.109 | 37.96 | 8.663 | 0.95104 | 30.69 | 0.80848 | 265.9 | 76.9 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/20/2020 | 7:21 | PSEL | FLI Proline |  |  |  |  | 7.298 | 39.628 | 51.2 | 1.82 | 35.537 | 204.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/4479_7_1_01172020_80.tiff | ./EL/4479_7_1_01172020_20.tiff | ./IV/4479_7_1_01202020.csv | 0 | 0 | 1 | ./RefIV/4479_7_1_01202020.csv | 8.862 | 8.862 | 1/20/2020 | 7:21 | 1.0178 | 0.97824
34 | 4480 |  | 7 | 1 |  | 16255.6 |  | multi-Si module |  |  | OE 0 days | 8.84 | 38.09 | 8.26 | 0.93439 | 31.48 | 0.82646 | 260 | 9.11 | 37.95 | 8.66 | 0.9506 | 30.71 | 0.80922 | 265.9 | 76.9 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/20/2020 | 7:23 | PSEL | FLI Proline |  |  |  |  | 7.298 | 39.59 | 51.2 | 1.835 | 35.462 | 204.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/4480_7_1_01172020_80.tiff | ./EL/4480_7_1_01172020_20.tiff | ./IV/4480_7_1_01202020.csv | 0 | 0 | 1 | ./RefIV/4480_7_1_01202020.csv | 8.862 | 8.862 | 1/20/2020 | 7:23 | 1.0174 | 0.97914
35 | 4475 |  | 7 | 1 |  | 16255.6 |  | multi-Si module |  |  | OE 0 days | 8.84 | 38.09 | 8.26 | 0.93439 | 31.48 | 0.82646 | 260 | 9.086 | 37.86 | 8.639 | 0.9508 | 30.48 | 0.80507 | 263.3 | 76.5 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/20/2020 | 7:09 | PSEL | FLI Proline |  |  |  |  | 7.273 | 39.59 | 51.2 | 1.82 | 35.341 | 204.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/4475_7_1_01172020_80.tiff | ./EL/4475_7_1_01172020_20.tiff | ./IV/4475_7_1_01202020.csv | 0 | 0 | 1 | ./RefIV/4475_7_1_01202020.csv | 8.862 | 8.862 | 1/20/2020 | 7:09 | 1.0176 | 0.97412
36 | 3602 |  | 24 | 4 |  | 16678.8 |  | mono-Si module |  |  | OE 0 days | 12.2 | 40.2 | 11.6 | 0.95082 | 32.4 | 0.80597 | 295 | 9.642 | 40.42 | 9.168 | 0.95084 | 32.69 | 0.80876 | 299.8 | 76.9 | 24.1 | back of panel |  | SPIRE | 4600SLP | 2017-08-05 | 10:17 | PSEL | FLI Proline |  |  |  |  | 7.203 | 42.142 | 57.6 | [7 empty] | 2.36 | 5/17/2017 |  |  |  | PSEL | ./EL/3602_24_4_05172017_80.tiff |  | ./IV/3602_24_4_05082017.csv | 0 | 1 | 2 | ./RefIV/3602_24_4_05082017.csv | 9.0256 | 9.0256 | 2017-08-05 | 10:17 | 1 | 1.0035
37 | 3602 |  | 24 | 4 |  | 16698.5 |  | mono-Si module |  |  | OE 1376 days | 12.2 | 40.2 | 11.6 | 0.95082 | 32.4 | 0.80597 | 295 | 9.463 | 40.19 | 8.967 | 0.94759 | 32.53 | 0.80941 | 291.7 | 76.7 | 25 | back of panel |  | SPIRE | 4600SLP | 2021-12-02 | 13:22 | PSEL | FLI Proline |  |  |  |  | 7.7 | 42.4 | 6.4 | 1.9 | 38.2 | 25.6 |  |  |  |  | 2.36 | 2/24/2021 |  | 2/24/2021 |  | PSEL | ./EL/3602_24_4_02242021_80.tiff | ./EL/3602_24_4_02242021_20.tiff | ./IV/3602_24_4_02122021.csv | 0 | 0 | 2 | ./RefIV/3602_24_4_02122021.csv | 8.862 | 9.0256 | 2017-08-05 | 10:17 | 0.9966 | 1.0043
38 | 3611 |  | 24 | 4 |  | 16678.8 |  | mono-Si module |  |  | OE 0 days | 12.2 | 40.2 | 11.6 | 0.95082 | 32.4 | 0.80597 | 295 | 9.648 | 40.56 | 9.179 | 0.95139 | 32.79 | 0.80843 | 301 | 76.9 | 24.5 | back of panel |  | SPIRE | 4600SLP | 2017-08-05 | 12:55 | PSEL | FLI Proline |  |  |  |  | 7.723 | 42.442 | 38.4 | [7 empty] | 2.36 | 5/17/2017 |  |  |  | PSEL | ./EL/3611_24_4_05172017_80.tiff |  | ./IV/3611_24_4_05082017.csv | 0 | 1 | 2 | ./RefIV/3611_24_4_05082017.csv | 9.0256 | 9.0256 | 2017-08-05 | 12:55 | 1.0006 | 1.0031
39 | 3611 |  | 24 | 4 |  | 16698.5 |  | mono-Si module |  |  | OE 1376 days | 12.2 | 40.2 | 11.6 | 0.95082 | 32.4 | 0.80597 | 295 | 9.44 | 40.26 | 8.978 | 0.95106 | 32.48 | 0.80676 | 291.6 | 76.7 | 25.3 | back of panel |  | SPIRE | 4600SLP | 2021-12-02 | 12:44 | PSEL | FLI Proline |  |  |  |  | 7.7 | 42.4 | 6.4 | 1.9 | 38.3 | 25.6 |  |  |  |  | 2.36 | 2/24/2021 |  | 2/24/2021 |  | PSEL | ./EL/3611_24_4_02242021_80.tiff | ./EL/3611_24_4_02242021_20.tiff | ./IV/3611_24_4_02122021.csv | 0 | 0 | 2 | ./RefIV/3611_24_4_02122021.csv | 8.862 | 9.0256 | 2017-08-05 | 12:55 | 1.0003 | 1.001
40 | 3610 |  | 24 | 4 |  | 16698.5 |  | mono-Si module |  |  | OE 1376 days | 12.2 | 40.2 | 11.6 | 0.95082 | 32.4 | 0.80597 | 295 | 9.47 | 39.98 | 8.966 | 0.94678 | 32.18 | 0.8049 | 288.5 | 76.2 | 24.8 | back of panel |  | SPIRE | 4600SLP | 2021-12-02 | 12:53 | PSEL | FLI Proline |  |  |  |  | 7.7 | 42.2 | 6.4 | 1.7 | 38.1 | 25.6 |  |  |  |  | 2.36 | 2/24/2021 |  | 2/24/2021 |  | PSEL | ./EL/3610_24_4_02242021_80.tiff | ./EL/3610_24_4_02242021_20.tiff | ./IV/3610_24_4_02122021.csv | 0 | 0 | 1 | ./RefIV/3610_24_4_02122021.csv | 8.862 | 9.0256 | 2017-08-05 | 12:39 | 0.99575 | 0.99868
41 | 3608 |  | 24 | 4 |  | 16698.5 |  | mono-Si module |  |  | OE 1376 days | 12.2 | 40.2 | 11.6 | 0.95082 | 32.4 | 0.80597 | 295 | 9.419 | 40.17 | 8.979 | 0.95329 | 32.45 | 0.80782 | 291.4 | 77 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2021-12-02 | 12:57 | PSEL | FLI Proline |  |  |  |  | 7.7 | 42.2 | 6.4 | 1.9 | 38.2 | 25.6 |  |  |  |  | 2.36 | 2/24/2021 |  | 2/24/2021 |  | PSEL | ./EL/3608_24_4_02242021_80.tiff | ./EL/3608_24_4_02242021_20.tiff | ./IV/3608_24_4_02122021.csv | 0 | 0 | 1 | ./RefIV/3608_24_4_02122021.csv | 8.862 | 9.0256 | 2017-08-05 | 12:04 | 1.0026 | 1.0023
42 | 3237 |  | 24 | 4 |  | 16698.5 |  | mono-Si module |  |  | OE 1022 days | 12.2 | 40.2 | 11.6 | 0.95082 | 32.4 | 0.80597 | 295 | 9.488 | 40.3 | 9.011 | 0.94973 | 32.5 | 0.80645 | 292.8 | 76.6 | 25.3 | back of panel |  | SPIRE | 4600SLP | 2021-12-02 | 10:57 | PSEL | FLI Proline |  |  |  |  | 7.598 | 42.142 | 6.4 | 1.905 | 37.939 | 25.6 |  |  |  |  | 2.36 | 2/24/2021 |  | 2/24/2021 |  | PSEL | ./EL/3237_24_4_02242021_80.tiff | ./EL/3237_24_4_02242021_20.tiff | ./IV/3237_24_4_02122021.csv | 0 | 0 | 1 | ./RefIV/3237_24_4_02122021.csv | 8.862 | 8.862 | 4/27/2018 | 11:51 | 0.99885 | 1.0006
43 | 3236 |  | 24 | 4 |  | 16698.5 |  | mono-Si module |  |  | OE 1022 days | 12.2 | 40.2 | 11.6 | 0.95082 | 32.4 | 0.80597 | 295 | 9.498 | 40.29 | 9.014 | 0.94904 | 32.46 | 0.80566 | 292.6 | 76.5 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-12-02 | 10:46 | PSEL | FLI Proline |  |  |  |  | 7.598 | 41.992 | 6.4 | 1.905 | 37.836 | 25.6 |  |  |  |  | 2.36 | 2/24/2021 |  | 2/24/2021 |  | PSEL | ./EL/3236_24_4_02242021_80.tiff | ./EL/3236_24_4_02242021_20.tiff | ./IV/3236_24_4_02122021.csv | 0 | 0 | 2 | ./RefIV/3236_24_4_02122021.csv | 8.862 | 8.862 | 4/27/2018 | 11:40 | 0.99813 | 0.99961
44 | 3236 |  | 24 | 4 |  | 16698.5 |  | mono-Si module |  |  | OE 1022 days | 12.2 | 40.2 | 11.6 | 0.95082 | 32.4 | 0.80597 | 295 | 9.498 | 40.29 | 9.014 | 0.94904 | 32.46 | 0.80566 | 292.6 | 76.5 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-12-02 | 10:46 | PSEL | FLI Proline | [7 empty] | 1.905 | 37.836 | 25.6 |  |  |  |  | 2.36 | 2/25/2021 |  | 2/25/2021 |  | PSEL |  | ./EL/3236_24_4_02252021_20.tiff | ./IV/3236_24_4_02122021.csv | 0 | 1 | 2 | ./RefIV/3236_24_4_02122021.csv | 8.862 | 8.862 | 4/27/2018 | 11:40 | 0.99813 | 0.99961
45 | 3609 |  | 24 | 4 |  | 16698.5 |  | mono-Si module |  |  | OE 1376 days | 12.2 | 40.2 | 11.6 | 0.95082 | 32.4 | 0.80597 | 295 | 9.431 | 40.28 | 8.99 | 0.95324 | 32.56 | 0.80834 | 292.7 | 77.1 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-12-02 | 12:40 | PSEL | FLI Proline |  |  |  |  | 7.7 | 42.5 | 6.4 | 1.9 | 38.3 | 25.6 |  |  |  |  | 2.36 | 2/24/2021 |  | 2/24/2021 |  | PSEL | ./EL/3609_24_4_02242021_80.tiff | ./EL/3609_24_4_02242021_20.tiff | ./IV/3609_24_4_02122021.csv | 0 | 0 | 1 | ./RefIV/3609_24_4_02122021.csv | 8.862 | 9.0256 | 2017-08-05 | 12:22 | 1.0025 | 1.0029
46 | 3603 |  | 24 | 4 |  | 16698.5 |  | mono-Si module |  |  | OE 1376 days | 12.2 | 40.2 | 11.6 | 0.95082 | 32.4 | 0.80597 | 295 | 9.468 | 40.09 | 9.004 | 0.95099 | 32.36 | 0.80718 | 291.4 | 76.8 | 25.3 | back of panel |  | SPIRE | 4600SLP | 2021-12-02 | 12:23 | PSEL | FLI Proline |  |  |  |  | 7.7 | 42.2 | 6.4 | 1.9 | 38.1 | 25.6 |  |  |  |  | 2.36 | 2/24/2021 |  | 2/24/2021 |  | PSEL | ./EL/3603_24_4_02242021_80.tiff | ./EL/3603_24_4_02242021_20.tiff | ./IV/3603_24_4_02122021.csv | 0 | 0 | 1 | ./RefIV/3603_24_4_02122021.csv | 8.862 | 9.0256 | 2017-08-05 | 10:54 | 1.0002 | 1.0015
47 | 3600 |  | 24 | 4 |  | 16698.5 |  | mono-Si module |  |  | OE 1022 days | 12.2 | 40.2 | 11.6 | 0.95082 | 32.4 | 0.80597 | 295 | 9.398 | 39.97 | 8.941 | 0.95137 | 32.23 | 0.80635 | 288.2 | 76.7 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2021-12-02 | 13:40 | PSEL | FLI Proline |  |  |  |  | 7.7 | 42.2 | 6.4 | 1.9 | 38 | 25.6 |  |  |  |  | 2.36 | 2/24/2021 |  | 2/24/2021 |  | PSEL | ./EL/3600_24_4_02242021_80.tiff | ./EL/3600_24_4_02242021_20.tiff | ./IV/3600_24_4_02122021.csv | 0 | 0 | 1 | ./RefIV/3600_24_4_02122021.csv | 8.862 | 8.862 | 4/27/2018 | 10:36 | 1.0006 | 1.0005
48 | 3607 |  | 24 | 4 |  | 16698.5 |  | mono-Si module |  |  | OE 1376 days | 12.2 | 40.2 | 11.6 | 0.95082 | 32.4 | 0.80597 | 295 | 9.421 | 40.28 | 9.01 | 0.95637 | 32.54 | 0.80785 | 293.2 | 77.3 | 24.8 | back of panel |  | SPIRE | 4600SLP | 2021-12-02 | 12:33 | PSEL | FLI Proline |  |  |  |  | 7.7 | 42.4 | 6.4 | 1.9 | 38.4 | 25.6 |  |  |  |  | 2.36 | 2/24/2021 |  | 2/24/2021 |  | PSEL | ./EL/3607_24_4_02242021_80.tiff | ./EL/3607_24_4_02242021_20.tiff | ./IV/3607_24_4_02122021.csv | 0 | 0 | 1 | ./RefIV/3607_24_4_02122021.csv | 8.862 | 9.0256 | 2017-08-05 | 11:50 | 1.0058 | 1.0023
49 | 3604 |  | 24 | 4 |  | 16698.5 |  | mono-Si module |  |  | OE 1376 days | 12.2 | 40.2 | 11.6 | 0.95082 | 32.4 | 0.80597 | 295 | 9.455 | 40.2 | 8.998 | 0.95167 | 32.37 | 0.80522 | 291.3 | 76.6 | 25 | back of panel |  | SPIRE | 4600SLP | 2021-12-02 | 12:49 | PSEL | FLI Proline |  |  |  |  | 7.7 | 42.4 | 6.4 | 1.9 | 32.8 | 25.6 |  |  |  |  | 2.36 | 2/24/2021 |  | 2/24/2021 |  | PSEL | ./EL/3604_24_4_02242021_80.tiff | ./EL/3604_24_4_02242021_20.tiff | ./IV/3604_24_4_02122021.csv | 0 | 0 | 1 | ./RefIV/3604_24_4_02122021.csv | 8.862 | 9.0256 | 2017-08-05 | 11:04 | 1.0009 | 0.99907
50 | 3932 |  | 24 | 2 |  | 16698.5 |  | mono-Si module |  |  | OE 1007 days | 11.4 | 39.2 | 10.8 | 0.94737 | 31.7 | 0.80867 | 270 | 9.069 | 38.61 | 8.604 | 0.94873 | 31.21 | 0.80834 | 268.5 | 76.7 | 25.3 | back of panel |  | SPIRE | 4600SLP | 2021-03-02 | 12:26 | PSEL | FLI Proline |  |  |  |  | 7.3 | 40.3 | 19.2 | 1.8 | 36.4 | 76.8 |  |  |  |  | 2.36 | 2/26/2021 |  | 2/26/2021 |  | PSEL | ./EL/3932_24_2_02262021_80.tiff | ./EL/3932_24_2_02262021_20.tiff | ./IV/3932_24_2_02032021.csv | 0 | 0 | 1 | ./RefIV/3932_24_2_02032021.csv | 8.862 | 8.862 | 2018-03-05 | 12:28 | 1.0014 | 0.99959
51 | 3933 |  | 24 | 2 |  | 16698.5 |  | mono-Si module |  |  | OE 1007 days | 11.4 | 39.2 | 10.8 | 0.94737 | 31.7 | 0.80867 | 270 | 9.094 | 38.81 | 8.643 | 0.95041 | 31.47 | 0.81087 | 271.9 | 77.1 | 24.8 | back of panel |  | SPIRE | 4600SLP | 2021-03-02 | 10:30 | PSEL | FLI Proline |  |  |  |  | 7.273 | 40.266 | 19.2 | 1.82 | 36.212 | 76.8 |  |  |  |  | 2.36 | 2/24/2021 |  | 2/24/2021 |  | PSEL | ./EL/3933_24_2_02242021_80.tiff | ./EL/3933_24_2_02242021_20.tiff | ./IV/3933_24_2_02032021.csv | 0 | 0 | 1 | ./RefIV/3933_24_2_02032021.csv | 8.862 | 8.862 | 2018-03-05 | 12:44 | 1.0032 | 1.0027
52 | 3502 |  | 24 | 2 |  | 16698.5 |  | mono-Si module |  |  | OE 1652 days | 11.4 | 39.2 | 10.8 | 0.94737 | 31.7 | 0.80867 | 270 | 9.057 | 38.85 | 8.605 | 0.95009 | 31.5 | 0.81081 | 271.1 | 77 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-03-02 | 14:18 | PSEL | FLI Proline |  |  |  |  | 7.3 | 40.5 | 19.2 | 1.8 | 36.6 | 76.8 |  |  |  |  | 2.36 | 2/26/2021 |  | 2/26/2021 |  | PSEL | ./EL/3502_24_2_02262021_80.tiff | ./EL/3502_24_2_02262021_20.tiff | ./IV/3502_24_2_02032021.csv | 0 | 0 | 1 | ./RefIV/3502_24_2_02032021.csv | 8.862 |  | 7/27/2016 | 12:01 | 1.0029 | 1.0026
53 | 3928 |  | 24 | 2 |  | 16698.5 |  | mono-Si module |  |  | OE 1007 days | 11.4 | 39.2 | 10.8 | 0.94737 | 31.7 | 0.80867 | 270 | 9.057 | 38.75 | 8.572 | 0.94645 | 31.4 | 0.81032 | 269.2 | 76.7 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-03-02 | 14:56 | PSEL | FLI Proline |  |  |  |  | 7.3 | 40.5 | 19.2 | 1.8 | 36.5 | 76.8 |  |  |  |  | 2.36 | 2/24/2021 |  | 2/24/2021 |  | PSEL | ./EL/3928_24_2_02242021_80.tiff | ./EL/3928_24_2_02242021_20.tiff | ./IV/3928_24_2_02032021.csv | 0 | 0 | 1 | ./RefIV/3928_24_2_02032021.csv | 8.862 | 8.862 | 2018-03-05 | 11:28 | 0.99903 | 1.002
54 | 3179 |  | 24 | 2 |  | 16698.5 |  | mono-Si module |  |  | OE 1885 days | 11.4 | 39.2 | 10.8 | 0.94737 | 31.7 | 0.80867 | 270 | 9.074 | 38.79 | 8.621 | 0.95008 | 31.52 | 0.81258 | 271.7 | 77.2 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2021-03-02 | 12:54 | PSEL | FLI Proline |  |  |  |  | 7.3 | 40.4 | 19.2 | 1.8 | 36.6 | 76.8 |  |  |  |  | 2.36 | 2/26/2021 |  | 2/26/2021 |  | PSEL | ./EL/3179_24_2_02262021_80.tiff | ./EL/3179_24_2_02262021_20.tiff | ./IV/3179_24_2_02032021.csv | 0 | 0 | 1 | ./RefIV/3179_24_2_02032021.csv | 8.862 |  | 2015-07-12 | 14:44 | 1.0029 | 1.0048
55 | 3277 |  | 24 | 2 |  | 16698.5 |  | mono-Si module |  |  | OE 1007 days | 11.4 | 39.2 | 10.8 | 0.94737 | 31.7 | 0.80867 | 270 | 9.052 | 38.91 | 8.627 | 0.95305 | 31.58 | 0.81162 | 272.5 | 77.4 | 24.6 | back of panel |  | SPIRE | 4600SLP | 2021-03-02 | 10:36 | PSEL | FLI Proline |  |  |  |  | 7.3 | 40.8 | 19.2 | 1.8 | 36.8 | 76.8 |  |  |  |  | 2.36 | 2/24/2021 |  | 2/24/2021 |  | PSEL | ./EL/3277_24_2_02242021_80.tiff | ./EL/3277_24_2_02242021_20.tiff | ./IV/3277_24_2_02032021.csv | 0 | 0 | 1 | ./RefIV/3277_24_2_02032021.csv | 8.862 | 8.862 | 2018-03-05 | 9:28 | 1.006 | 1.0036
56 | 3923 |  | 24 | 2 |  | 16698.5 |  | mono-Si module |  |  | OE 1007 days | 11.4 | 39.2 | 10.8 | 0.94737 | 31.7 | 0.80867 | 270 | 9.109 | 38.75 | 8.635 | 0.94796 | 31.27 | 0.80697 | 270 | 76.5 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-03-02 | 14:42 | PSEL | FLI Proline |  |  |  |  | 7.3 | 41.5 | 19.2 | 1.8 | 37.1 | 76.8 |  |  |  |  | 2.36 | 2/26/2021 |  | 2/26/2021 |  | PSEL | ./EL/3923_24_2_02262021_80.tiff | ./EL/3923_24_2_02262021_20.tiff | ./IV/3923_24_2_02032021.csv | 0 | 0 | 1 | ./RefIV/3923_24_2_02032021.csv | 8.862 | 8.862 | 2018-03-05 | 9:57 | 1.0006 | 0.99789
57 | 3929 |  | 24 | 2 |  | 16698.5 |  | mono-Si module |  |  | OE 1007 days | 11.4 | 39.2 | 10.8 | 0.94737 | 31.7 | 0.80867 | 270 | 9.055 | 38.74 | 8.588 | 0.94843 | 31.34 | 0.80898 | 269.2 | 76.7 | 25 | back of panel |  | SPIRE | 4600SLP | 2021-03-02 | 10:47 | PSEL | FLI Proline |  |  |  |  | 7.3 | 40.4 | 19.2 | 1.8 | 36.4 | 76.8 |  |  |  |  | 2.36 | 2/26/2021 |  | 2/26/2021 |  | PSEL | ./EL/3929_24_2_02262021_80.tiff | ./EL/3929_24_2_02262021_20.tiff | ./IV/3929_24_2_02032021.csv | 0 | 0 | 1 | ./RefIV/3929_24_2_02032021.csv | 8.862 | 8.862 | 2018-03-05 | 11:38 | 1.0011 | 1.0004
58 | 3504 |  | 24 | 2 |  | 16698.5 |  | mono-Si module |  |  | OE 1652 days | 11.4 | 39.2 | 10.8 | 0.94737 | 31.7 | 0.80867 | 270 | 9.149 | 38.92 | 8.681 | 0.94885 | 31.58 | 0.81141 | 274.1 | 77 | 24.7 | back of panel |  | SPIRE | 4600SLP | 2021-03-02 | 12:49 | PSEL | FLI Proline |  |  |  |  | 7.3 | 41 | 19.2 | 1.8 | 36.7 | 76.8 |  |  |  |  | 2.36 | 2/26/2021 |  | 2/26/2021 |  | PSEL | ./EL/3504_24_2_02262021_80.tiff | ./EL/3504_24_2_02262021_20.tiff | ./IV/3504_24_2_02032021.csv | 0 | 0 | 1 | ./RefIV/3504_24_2_02032021.csv | 8.862 |  | 7/27/2016 | 11:30 | 1.0016 | 1.0034
59 | 3501 |  | 24 | 2 |  | 16698.5 |  | mono-Si module |  |  | OE 1652 days | 11.4 | 39.2 | 10.8 | 0.94737 | 31.7 | 0.80867 | 270 | 9.045 | 38.76 | 8.563 | 0.94671 | 31.44 | 0.81115 | 269.2 | 76.8 | 24.7 | back of panel |  | SPIRE | 4600SLP | 2021-03-02 | 12:34 | PSEL | FLI Proline |  |  |  |  | 7.3 | 40.4 | 19.2 | 1.8 | 36.5 | 76.8 |  |  |  |  | 2.36 | 2/26/2021 |  | 2/26/2021 |  | PSEL | ./EL/3501_24_2_02262021_80.tiff | ./EL/3501_24_2_02262021_20.tiff | ./IV/3501_24_2_02032021.csv | 0 | 0 | 2 | ./RefIV/3501_24_2_02032021.csv | 8.862 |  | 7/27/2016 | 12:20 | 0.99931 | 1.0031
60 | 3500 |  | 24 | 2 |  | 16698.5 |  | mono-Si module |  |  | OE 1652 days | 11.4 | 39.2 | 10.8 | 0.94737 | 31.7 | 0.80867 | 270 | 9.131 | 38.87 | 8.66 | 0.94842 | 31.55 | 0.81168 | 273.2 | 77 | 25 | back of panel |  | SPIRE | 4600SLP | 2021-03-02 | 14:25 | PSEL | FLI Proline |  |  |  |  | 7.3 | 40.6 | 19.2 | 1.8 | 36.6 | 76.8 |  |  |  |  | 2.36 | 2/26/2021 |  | 2/26/2021 |  | PSEL | ./EL/3500_24_2_02262021_80.tiff | ./EL/3500_24_2_02262021_20.tiff | ./IV/3500_24_2_02032021.csv | 0 | 0 | 1 | ./RefIV/3500_24_2_02032021.csv | 8.862 |  | 7/27/2016 | 12:49 | 1.0011 | 1.0037
61 | 3926 |  | 24 | 2 |  | 16698.5 |  | mono-Si module |  |  | OE 1007 days | 11.4 | 39.2 | 10.8 | 0.94737 | 31.7 | 0.80867 | 270 | 9.089 | 38.83 | 8.626 | 0.94906 | 31.46 | 0.8102 | 271.3 | 76.9 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-03-02 | 14:31 | PSEL | FLI Proline |  |  |  |  | 7.3 | 40.5 | 19.2 | 1.8 | 36.6 | 76.8 |  |  |  |  | 2.36 | 2/26/2021 |  | 2/26/2021 |  | PSEL | ./EL/3926_24_2_02262021_80.tiff | ./EL/3926_24_2_02262021_20.tiff | ./IV/3926_24_2_02032021.csv | 0 | 0 | 1 | ./RefIV/3926_24_2_02032021.csv | 8.862 | 8.862 | 2018-03-05 | 10:57 | 1.0018 | 1.0019
62 | 3503 |  | 24 | 2 |  | 16698.5 |  | mono-Si module |  |  | OE 1652 days | 11.4 | 39.2 | 10.8 | 0.94737 | 31.7 | 0.80867 | 270 | 9.052 | 38.59 | 8.593 | 0.94929 | 31.17 | 0.80772 | 267.8 | 76.7 | 25.3 | back of panel |  | SPIRE | 4600SLP | 2021-03-02 | 15:03 | PSEL | FLI Proline |  |  |  |  | 7.3 | 40.4 | 19.2 | 1.8 | 36.4 | 76.8 |  |  |  |  | 2.36 | 2/24/2021 |  | 2/24/2021 |  | PSEL | ./EL/3503_24_2_02242021_80.tiff | ./EL/3503_24_2_02242021_20.tiff | ./IV/3503_24_2_02032021.csv | 0 | 0 | 1 | ./RefIV/3503_24_2_02032021.csv | 8.862 |  | 7/27/2016 | 11:48 | 1.002 | 0.99882
63 | 3930 |  | 24 | 2 |  | 16698.5 |  | mono-Si module |  |  | OE 1007 days | 11.4 | 39.2 | 10.8 | 0.94737 | 31.7 | 0.80867 | 270 | 9.039 | 38.58 | 8.577 | 0.94889 | 31.18 | 0.80819 | 267.4 | 76.7 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2021-03-02 | 12:42 | PSEL | FLI Proline |  |  |  |  | 7.3 | 40.3 | 19.2 | 1.8 | 36.4 | 76.8 |  |  |  |  | 2.36 | 2/26/2021 |  | 2/26/2021 |  | PSEL | ./EL/3930_24_2_02262021_80.tiff | ./EL/3930_24_2_02262021_20.tiff | ./IV/3930_24_2_02032021.csv | 0 | 0 | 1 | ./RefIV/3930_24_2_02032021.csv | 8.862 | 8.862 | 2018-03-05 | 12:09 | 1.0016 | 0.9994
64 | 3931 |  | 24 | 2 |  | 16698.5 |  | mono-Si module |  |  | OE 1007 days | 11.4 | 39.2 | 10.8 | 0.94737 | 31.7 | 0.80867 | 270 | 9.113 | 38.93 | 8.63 | 0.947 | 31.6 | 0.81171 | 272.7 | 76.9 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2021-03-02 | 15:16 | PSEL | FLI Proline |  |  |  |  | 7.3 | 40.8 | 19.2 | 1.8 | 37 | 76.8 |  |  |  |  | 2.36 | 2/24/2021 |  | 2/24/2021 |  | PSEL | ./EL/3931_24_2_02242021_80.tiff | ./EL/3931_24_2_02242021_20.tiff | ./IV/3931_24_2_02032021.csv | 0 | 0 | 1 | ./RefIV/3931_24_2_02032021.csv | 8.862 | 8.862 | 2018-03-05 | 12:19 | 0.99961 | 1.0038
65 | 3927 |  | 24 | 2 |  | 16698.5 |  | mono-Si module |  |  | OE 1007 days | 11.4 | 39.2 | 10.8 | 0.94737 | 31.7 | 0.80867 | 270 | 9.07 | 38.83 | 8.61 | 0.94928 | 31.53 | 0.812 | 271.5 | 77.1 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-03-02 | 15:09 | PSEL | FLI Proline |  |  |  |  | 7.3 | 40.6 | 19.2 | 1.8 | 36.7 | 76.8 |  |  |  |  | 2.36 | 2/24/2021 |  | 2/24/2021 |  | PSEL | ./EL/3927_24_2_02242021_80.tiff | ./EL/3927_24_2_02242021_20.tiff | ./IV/3927_24_2_02032021.csv | 0 | 0 | 1 | ./RefIV/3927_24_2_02032021.csv | 8.862 | 8.862 | 2018-03-05 | 11:18 | 1.002 | 1.0041
66 | 3924 |  | 24 | 2 |  | 16698.5 |  | mono-Si module |  |  | OE 1007 days | 11.4 | 39.2 | 10.8 | 0.94737 | 31.7 | 0.80867 | 270 | 9.142 | 38.83 | 8.685 | 0.95001 | 31.49 | 0.81097 | 273.5 | 77.1 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-03-02 | 15:21 | PSEL | FLI Proline |  |  |  |  | 7.3 | 40.8 | 19.2 | 1.8 | 36.9 | 76.8 |  |  |  |  | 2.36 | 2/24/2021 |  | 2/24/2021 |  | PSEL | ./EL/3924_24_2_02242021_80.tiff | ./EL/3924_24_2_02242021_20.tiff | ./IV/3924_24_2_02032021.csv | 0 | 0 | 1 | ./RefIV/3924_24_2_02032021.csv | 8.862 | 8.862 | 2018-03-05 | 10:19 | 1.0028 | 1.0028
67 | 3925 |  | 24 | 2 |  | 16698.5 |  | mono-Si module |  |  | OE 1007 days | 11.4 | 39.2 | 10.8 | 0.94737 | 31.7 | 0.80867 | 270 | 9.07 | 38.72 | 8.61 | 0.94928 | 31.31 | 0.80863 | 269.5 | 76.8 | 25.4 | back of panel |  | SPIRE | 4600SLP | 2021-03-02 | 15:26 | PSEL | FLI Proline |  |  |  |  | 7.3 | 40.6 | 19.2 | 1.8 | 36.7 | 76.8 |  |  |  |  | 2.36 | 2/24/2021 |  | 2/24/2021 |  | PSEL | ./EL/3925_24_2_02242021_80.tiff | ./EL/3925_24_2_02242021_20.tiff | ./IV/3925_24_2_02032021.csv | 0 | 0 | 1 | ./RefIV/3925_24_2_02032021.csv | 8.862 | 8.862 | 2018-03-05 | 10:46 | 1.002 | 0.99994
68 | 4765 |  | 24 | 3 |  | 16693.6 |  | mono-Si module |  |  | OE 0 days | 12 | 40.2 | 11.4 | 0.95 | 32.4 | 0.80597 | 290 | 9.44 | 39.95 | 8.977 | 0.95095 | 31.94 | 0.7995 | 286.8 | 76 | 25.3 | back of panel |  | SPIRE | 4600SLP | 2/26/2021 | 11:43 | PSEL | FLI Proline |  |  |  |  | 7.6 | 41.7 | 6.4 | 1.9 | 37.6 | 38.4 |  |  |  |  | 2.36 | 2021-01-03 |  | 2021-01-03 |  | PSEL | ./EL/4765_24_3_03012021_80.tiff | ./EL/4765_24_3_03012021_20.tiff | ./IV/4765_24_3_02262021.csv | 0 | 0 | 1 | ./RefIV/4765_24_3_02262021.csv | 8.862 | 8.862 | 2/26/2021 | 11:43 | 1.001 | 0.99197
69 | 4760 |  | 24 | 3 |  | 16693.6 |  | mono-Si module |  |  | OE 0 days | 12 | 40.2 | 11.4 | 0.95 | 32.4 | 0.80597 | 290 | 9.479 | 40.03 | 8.997 | 0.94915 | 31.97 | 0.79865 | 287.6 | 75.8 | 24.8 | back of panel |  | SPIRE | 4600SLP | 2/26/2021 | 10:28 | PSEL | FLI Proline |  |  |  |  | 7.6 | 41.9 | 6.4 | 1.9 | 37.7 | 38.4 |  |  |  |  | 2.36 | 2021-01-03 |  | 2021-01-03 |  | PSEL | ./EL/4760_24_3_03012021_80.tiff | ./EL/4760_24_3_03012021_20.tiff | ./IV/4760_24_3_02262021.csv | 0 | 0 | 1 | ./RefIV/4760_24_3_02262021.csv | 8.862 | 8.862 | 2/26/2021 | 10:28 | 0.99911 | 0.99092
70 | 4764 |  | 24 | 3 |  | 16693.6 |  | mono-Si module |  |  | OE 0 days | 12 | 40.2 | 11.4 | 0.95 | 32.4 | 0.80597 | 290 | 9.509 | 39.87 | 8.98 | 0.94437 | 31.92 | 0.8006 | 286.6 | 75.6 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2/26/2021 | 11:39 | PSEL | FLI Proline |  |  |  |  | 7.6 | 41.9 | 6.4 | 1.9 | 37.6 | 38.4 |  |  |  |  | 2.36 | 2021-01-03 |  | 2021-01-03 |  | PSEL | ./EL/4764_24_3_03012021_80.tiff | ./EL/4764_24_3_03012021_20.tiff | ./IV/4764_24_3_02262021.csv | 0 | 0 | 1 | ./RefIV/4764_24_3_02262021.csv | 8.862 | 8.862 | 2/26/2021 | 11:39 | 0.99407 | 0.99334
71 | 10105 |  | 24 | 3 |  | 16698.5 |  | mono-Si module |  |  | OE 1361 days | 12 | 40.2 | 11.4 | 0.95 | 32.4 | 0.80597 | 290 | 9.442 | 39.87 | 8.995 | 0.95266 | 31.96 | 0.80161 | 287.5 | 76.4 | 25.4 | back of panel |  | SPIRE | 4600SLP | 2021-12-02 | 14:09 | PSEL | FLI Proline |  |  |  |  | 7.6 | 41.7 | 6.4 | 1.9 | 37.6 | 38.4 |  |  |  |  | 2.36 | 2021-01-03 |  | 2021-01-03 |  | PSEL | ./EL/10105_24_3_03012021_80.tiff | ./EL/10105_24_3_03012021_20.tiff | ./IV/10105_24_3_02122021.csv | 0 | 0 | 1 | ./RefIV/10105_24_3_02122021.csv | 8.862 | 8.714 | 5/23/2017 | 13:24 | 1.0028 | 0.99458
72 | 10196 |  | 24 | 3 |  | 16698.5 |  | mono-Si module |  |  | OE 1576 days | 12 | 40.2 | 11.4 | 0.95 | 32.4 | 0.80597 | 290 | 9.458 | 39.99 | 8.989 | 0.95041 | 32.09 | 0.80245 | 288.5 | 76.3 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-12-02 | 13:31 | PSEL | FLI Proline |  |  |  |  | 7.6 | 41.9 | 6.4 | 1.9 | 37.8 | 38.4 |  |  |  |  | 2.36 | 2021-01-03 |  | 2021-01-03 |  | PSEL | ./EL/10196_24_3_03012021_80.tiff | ./EL/10196_24_3_03012021_20.tiff | ./IV/10196_24_3_02122021.csv | 0 | 0 | 1 | ./RefIV/10196_24_3_02122021.csv | 8.862 |  | 10/20/2016 | 16:17 | 1.0004 | 0.99563
73 | 3401 |  | 24 | 3 |  | 16698.5 |  | mono-Si module |  |  | OE 1017 days | 12 | 40.2 | 11.4 | 0.95 | 32.4 | 0.80597 | 290 | 9.48 | 39.88 | 8.966 | 0.94578 | 32.1 | 0.80491 | 287.8 | 76.1 | 24.8 | back of panel |  | SPIRE | 4600SLP | 2021-12-02 | 14:14 | PSEL | FLI Proline |  |  |  |  | 7.6 | 41.7 | 6.4 | 1.9 | 37.6 | 38.4 |  |  |  |  | 2.36 | 2021-01-03 |  | 2021-01-03 |  | PSEL | ./EL/3401_24_3_03012021_80.tiff | ./EL/3401_24_3_03012021_20.tiff | ./IV/3401_24_3_02122021.csv | 0 | 0 | 1 | ./RefIV/3401_24_3_02122021.csv | 8.862 | 8.862 | 2018-02-05 | 10:41 | 0.99556 | 0.99869
74 | 4762 |  | 24 | 3 |  | 16693.6 |  | mono-Si module |  |  | OE 0 days | 12 | 40.2 | 11.4 | 0.95 | 32.4 | 0.80597 | 290 | 9.443 | 39.9 | 8.989 | 0.95192 | 31.88 | 0.799 | 286.5 | 76.1 | 25 | back of panel |  | SPIRE | 4600SLP | 2/26/2021 | 11:31 | PSEL | FLI Proline |  |  |  |  | 7.6 | 41.7 | 6.4 | 1.9 | 37.6 | 38.4 |  |  |  |  | 2.36 | 2021-01-03 |  | 2021-01-03 |  | PSEL | ./EL/4762_24_3_03012021_80.tiff | ./EL/4762_24_3_03012021_20.tiff | ./IV/4762_24_3_02262021.csv | 0 | 0 | 1 | ./RefIV/4762_24_3_02262021.csv | 8.862 | 8.862 | 2/26/2021 | 11:31 | 1.002 | 0.99135
75 | 4761 |  | 24 | 3 |  | 16693.6 |  | mono-Si module |  |  | OE 0 days | 12 | 40.2 | 11.4 | 0.95 | 32.4 | 0.80597 | 290 | 9.456 | 39.98 | 8.982 | 0.94987 | 31.98 | 0.7999 | 287.2 | 76 | 25 | back of panel |  | SPIRE | 4600SLP | 2/26/2021 | 11:26 | PSEL | FLI Proline |  |  |  |  | 7.6 | 41.7 | 6.4 | 1.9 | 37.7 | 38.4 |  |  |  |  | 2.36 | 2021-01-03 |  | 2021-01-03 |  | PSEL | ./EL/4761_24_3_03012021_80.tiff | ./EL/4761_24_3_03012021_20.tiff | ./IV/4761_24_3_02262021.csv | 0 | 0 | 1 | ./RefIV/4761_24_3_02262021.csv | 8.862 | 8.862 | 2/26/2021 | 11:26 | 0.99987 | 0.99247
76 | 4763 |  | 24 | 3 |  | 16693.6 |  | mono-Si module |  |  | OE 0 days | 12 | 40.2 | 11.4 | 0.95 | 32.4 | 0.80597 | 290 | 9.453 | 40.03 | 8.989 | 0.95092 | 32.03 | 0.80015 | 287.9 | 76.1 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2/26/2021 | 11:35 | PSEL | FLI Proline |  |  |  |  | 7.6 | 41.7 | 6.4 | 1.9 | 37.6 | 38.4 |  |  |  |  | 2.36 | 2021-01-03 |  | 2021-01-03 |  | PSEL | ./EL/4763_24_3_03012021_80.tiff | ./EL/4763_24_3_03012021_20.tiff | ./IV/4763_24_3_02262021.csv | 0 | 0 | 1 | ./RefIV/4763_24_3_02262021.csv | 8.862 | 8.862 | 2/26/2021 | 11:35 | 1.001 | 0.99278
77 | 10195 |  | 24 | 3 |  | 16698.5 |  | mono-Si module |  |  | OE 1576 days | 12 | 40.2 | 11.4 | 0.95 | 32.4 | 0.80597 | 290 | 9.462 | 39.85 | 8.99 | 0.95012 | 32.05 | 0.80427 | 288.2 | 76.4 | 25.3 | back of panel |  | SPIRE | 4600SLP | 2021-12-02 | 14:20 | PSEL | FLI Proline |  |  |  |  | 7.6 | 41.7 | 6.4 | 1.9 | 37.6 | 38.4 |  |  |  |  | 2.36 | 2021-01-03 |  | 2021-01-03 |  | PSEL | ./EL/10195_24_3_03012021_80.tiff | ./EL/10195_24_3_03012021_20.tiff | ./IV/10195_24_3_02122021.csv | 0 | 0 | 1 | ./RefIV/10195_24_3_02122021.csv | 8.862 |  | 10/20/2016 | 16:02 | 1.0001 | 0.99789
78 | 3400 |  | 24 | 3 |  | 16698.5 |  | mono-Si module |  |  | OE 1017 days | 12 | 40.2 | 11.4 | 0.95 | 32.4 | 0.80597 | 290 | 9.477 | 40.16 | 9.008 | 0.95051 | 32.23 | 0.80254 | 290.3 | 76.3 | 24.7 | back of panel |  | SPIRE | 4600SLP | 2021-12-02 | 13:09 | PSEL | FLI Proline |  |  |  |  | 7.6 | 42 | 6.4 | 1.9 | 37.8 | 38.4 |  |  |  |  | 2.36 | 2021-01-03 |  | 2021-01-03 |  | PSEL | ./EL/3400_24_3_03012021_80.tiff | ./EL/3400_24_3_03012021_20.tiff | ./IV/3400_24_3_02122021.csv | 0 | 0 | 1 | ./RefIV/3400_24_3_02122021.csv | 8.862 | 8.862 | 2018-02-05 | 10:29 | 1.0005 | 0.99574
79 | 10109 |  | 24 | 3 |  | 16698.5 |  | mono-Si module |  |  | OE 1361 days | 12 | 40.2 | 11.4 | 0.95 | 32.4 | 0.80597 | 290 | 9.454 | 39.97 | 8.988 | 0.95071 | 32.14 | 0.8041 | 288.9 | 76.5 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-12-02 | 14:03 | PSEL | FLI Proline |  |  |  |  | 7.6 | 41.7 | 6.4 | 1.9 | 37.6 | 38.4 |  |  |  |  | 2.36 | 2021-01-03 |  | 2021-01-03 |  | PSEL | ./EL/10109_24_3_03012021_80.tiff | ./EL/10109_24_3_03012021_20.tiff | ./IV/10109_24_3_02122021.csv | 0 | 0 | 1 | ./RefIV/10109_24_3_02122021.csv | 8.862 | 8.714 | 5/23/2017 | 13:33 | 1.0007 | 0.99768
80 | 3404 |  | 24 | 3 |  | 16698.5 |  | mono-Si module |  |  | OE 1017 days | 12 | 40.2 | 11.4 | 0.95 | 32.4 | 0.80597 | 290 | 9.495 | 40.03 | 9.01 | 0.94892 | 32.16 | 0.8034 | 289.7 | 76.2 | 24.7 | back of panel |  | SPIRE | 4600SLP | 2021-12-02 | 13:14 | PSEL | FLI Proline |  |  |  |  | 7.6 | 42 | 6.4 | 1.9 | 42 | 38.4 |  |  |  |  | 2.36 | 2021-01-03 |  | 2021-01-03 |  | PSEL | ./EL/3404_24_3_03012021_80.tiff | ./EL/3404_24_3_03012021_20.tiff | ./IV/3404_24_3_02122021.csv | 0 | 0 | 1 | ./RefIV/3404_24_3_02122021.csv | 8.862 | 8.862 | 2018-02-05 | 11:43 | 0.99886 | 0.99681
81 | 3399 |  | 24 | 3 |  | 16698.5 |  | mono-Si module |  |  | OE 1017 days | 12 | 40.2 | 11.4 | 0.95 | 32.4 | 0.80597 | 290 | 9.508 | 40.13 | 9.031 | 0.94983 | 32.15 | 0.80115 | 290.4 | 76.1 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-12-02 | 13:03 | PSEL | FLI Proline |  |  |  |  | 7.623 | 41.917 | 6.4 | 1.905 | 37.601 | 38.4 |  |  |  |  | 2.36 | 2021-01-03 |  | 2021-01-03 |  | PSEL | ./EL/3399_24_3_03012021_80.tiff | ./EL/3399_24_3_03012021_20.tiff | ./IV/3399_24_3_02122021.csv | 0 | 0 | 1 | ./RefIV/3399_24_3_02122021.csv | 8.862 | 8.862 | 2018-02-05 | 10:08 | 0.99982 | 0.99401
82 | 3402 |  | 24 | 3 |  | 16698.5 |  | mono-Si module |  |  | OE 1017 days | 12 | 40.2 | 11.4 | 0.95 | 32.4 | 0.80597 | 290 | 9.442 | 39.94 | 9.005 | 0.95372 | 32.09 | 0.80346 | 289 | 76.6 | 25 | back of panel |  | SPIRE | 4600SLP | 2021-12-02 | 13:56 | PSEL | FLI Proline |  |  |  |  | 7.6 | 41.7 | 6.4 | 1.9 | 37.6 | 38.4 |  |  |  |  | 2.36 | 2021-01-03 |  | 2021-01-03 |  | PSEL | ./EL/3402_24_3_03012021_80.tiff | ./EL/3402_24_3_03012021_20.tiff | ./IV/3402_24_3_02122021.csv | 0 | 0 | 1 | ./RefIV/3402_24_3_02122021.csv | 8.862 | 8.862 | 2018-02-05 | 10:55 | 1.0039 | 0.99688
83 | 4173 |  | 15 | 3 |  | 16335 |  | multi-Si module |  |  | OE 886 days | 9.09 | 38.8 | 8.52 | 0.93729 | 31.7 | 0.81701 | 270 | 9.1 | 37.63 | 8.64 | 0.94945 | 30.43 | 0.80866 | 262.9 | 76.8 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 15:53 | PSEL | FLI Proline | [7 empty] | 1.83 | 34.636 | 153.6 |  |  |  |  | 2.36 | 2021-03-02 |  | 2021-03-02 |  | PSEL |  | ./EL/4173_15_3_02032021_20.tiff | ./IV/4173_15_3_02012021.csv | 0 | 1 | 2 | ./RefIV/4173_15_3_02012021.csv | 8.862 | 8.862 | 8/30/2018 | 15:49 | 1.013 | 0.98978
84 | 4173 |  | 15 | 3 |  | 16335 |  | multi-Si module |  |  | OE 517 days | 9.09 | 38.8 | 8.52 | 0.93729 | 31.7 | 0.81701 | 270 | 9.174 | 37.82 | 8.719 | 0.9504 | 30.7 | 0.81174 | 267.7 | 77.1 | 25.3 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 9:14 | PSEL | FLI Proline |  |  |  |  | 7.363 | 39.365 | 38.4 | 1.845 | 35.274 | 204.6 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4173_15_3_01302020_80.tiff | ./EL/4173_15_3_01302020_20.tiff | ./IV/4173_15_3_01292020.csv | 0 | 0 | 2 | ./RefIV/4173_15_3_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 15:49 | 1.014 | 0.99355
85 | 4175 |  | 15 | 3 |  | 16335 |  | multi-Si module |  |  | OE 886 days | 9.09 | 38.8 | 8.52 | 0.93729 | 31.7 | 0.81701 | 270 | 9.094 | 37.63 | 8.637 | 0.94975 | 30.43 | 0.80866 | 262.8 | 76.8 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 15:53 | PSEL | FLI Proline |  |  |  |  | 7.323 | 38.839 | 38.4 | 1.83 | 34.636 | 153.6 |  |  |  |  | 2.36 | 2021-03-02 |  | 2021-03-02 |  | PSEL | ./EL/4175_15_3_02032021_80.tiff | ./EL/4175_15_3_02032021_20.tiff | ./IV/4175_15_3_02012021.csv | 0 | 1 | 2 | ./RefIV/4175_15_3_02012021.csv | 8.862 | 8.862 | 8/30/2018 | 16:00 | 1.0133 | 0.98978
86 | 4175 |  | 15 | 3 |  | 16335 |  | multi-Si module |  |  | OE 517 days | 9.09 | 38.8 | 8.52 | 0.93729 | 31.7 | 0.81701 | 270 | 9.173 | 37.85 | 8.719 | 0.95051 | 30.64 | 0.80951 | 267.2 | 76.9 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 9:21 | PSEL | FLI Proline |  |  |  |  | 7.368 | 39.473 | 38.4 | 1.845 | 35.387 | 204.6 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4175_15_3_01302020_80.tiff | ./EL/4175_15_3_01302020_20.tiff | ./IV/4175_15_3_01292020.csv | 0 | 0 | 2 | ./RefIV/4175_15_3_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 16:00 | 1.0141 | 0.99082
87 | 4178 |  | 15 | 3 |  | 16335 |  | multi-Si module |  |  | OE 886 days | 9.09 | 38.8 | 8.52 | 0.93729 | 31.7 | 0.81701 | 270 | 9.092 | 37.64 | 8.653 | 0.95172 | 30.41 | 0.80792 | 263.1 | 76.9 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 15:52 | PSEL | FLI Proline |  |  |  |  | 7.328 | 38.914 | 38.4 | 1.83 | 34.589 | 153.6 |  |  |  |  | 2.36 | 2021-03-02 |  | 2021-03-02 |  | PSEL | ./EL/4178_15_3_02032021_80.tiff | ./EL/4178_15_3_02032021_20.tiff | ./IV/4178_15_3_02012021.csv | 0 | 1 | 2 | ./RefIV/4178_15_3_02012021.csv | 8.862 | 8.862 | 8/30/2018 | 16:10 | 1.0154 | 0.98887
88 | 4178 |  | 15 | 3 |  | 16335 |  | multi-Si module |  |  | OE 517 days | 9.09 | 38.8 | 8.52 | 0.93729 | 31.7 | 0.81701 | 270 | 9.175 | 37.83 | 8.722 | 0.95063 | 30.69 | 0.81126 | 267.6 | 77.1 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 9:44 | PSEL | FLI Proline |  |  |  |  | 7.363 | 39.365 | 38.4 | 1.845 | 35.274 | 204.6 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4178_15_3_01302020_80.tiff | ./EL/4178_15_3_01302020_20.tiff | ./IV/4178_15_3_01292020.csv | 0 | 0 | 2 | ./RefIV/4178_15_3_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 16:10 | 1.0142 | 0.99296
89 | 4174 |  | 15 | 3 |  | 16335 |  | multi-Si module |  |  | OE 886 days | 9.09 | 38.8 | 8.52 | 0.93729 | 31.7 | 0.81701 | 270 | 9.199 | 37.75 | 8.713 | 0.94717 | 30.48 | 0.80742 | 265.6 | 76.5 | 25 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 15:46 | PSEL | FLI Proline |  |  |  |  | 7.323 | 39.027 | 38.4 | 1.83 | 34.899 | 204.6 |  |  |  |  | 2.36 | 2021-03-02 |  | 2021-03-02 |  | PSEL | ./EL/4174_15_3_02032021_80.tiff | ./EL/4174_15_3_02032021_20.tiff | ./IV/4174_15_3_02012021.csv | 0 | 1 | 2 | ./RefIV/4174_15_3_02012021.csv | 8.862 | 8.862 | 8/30/2018 | 15:56 | 1.0105 | 0.98826
90 | 4174 |  | 15 | 3 |  | 16335 |  | multi-Si module |  |  | OE 517 days | 9.09 | 38.8 | 8.52 | 0.93729 | 31.7 | 0.81701 | 270 | 9.222 | 37.82 | 8.748 | 0.9486 | 30.56 | 0.80804 | 267.3 | 76.6 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 9:16 | PSEL | FLI Proline |  |  |  |  | 7.363 | 39.703 | 38.4 | 1.81 | 35.349 | 204.6 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4174_15_3_01302020_80.tiff | ./EL/4174_15_3_01302020_20.tiff | ./IV/4174_15_3_01292020.csv | 0 | 0 | 2 | ./RefIV/4174_15_3_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 15:56 | 1.0121 | 0.98902
91 | 4176 |  | 15 | 3 |  | 16335 |  | multi-Si module |  |  | OE 886 days | 9.09 | 38.8 | 8.52 | 0.93729 | 31.7 | 0.81701 | 270 | 9.197 | 37.74 | 8.719 | 0.94803 | 30.44 | 0.80657 | 265.4 | 76.5 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 15:49 | PSEL | FLI Proline |  |  |  |  | 7.323 | 38.99 | 38.4 | 1.83 | 34.786 | 204.6 |  |  |  |  | 2.36 | 2021-03-02 |  | 2021-03-02 |  | PSEL | ./EL/4176_15_3_02032021_80.tiff | ./EL/4176_15_3_02032021_20.tiff | ./IV/4176_15_3_02012021.csv | 0 | 1 | 2 | ./RefIV/4176_15_3_02012021.csv | 8.862 | 8.862 | 8/30/2018 | 16:03 | 1.0115 | 0.98722
92 | 4176 |  | 15 | 3 |  | 16335 |  | multi-Si module |  |  | OE 517 days | 9.09 | 38.8 | 8.52 | 0.93729 | 31.7 | 0.81701 | 270 | 9.227 | 37.83 | 8.757 | 0.94906 | 30.63 | 0.80967 | 268.2 | 76.9 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 9:43 | PSEL | FLI Proline |  |  |  |  | 7.363 | 39.553 | 38.4 | 1.84 | 35.349 | 204.6 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4176_15_3_01302020_80.tiff | ./EL/4176_15_3_01302020_20.tiff | ./IV/4176_15_3_01292020.csv | 0 | 0 | 2 | ./RefIV/4176_15_3_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 16:03 | 1.0126 | 0.99102
93 | 4181 |  | 15 | 3 |  | 16335 |  | multi-Si module |  |  | OE 886 days | 9.09 | 38.8 | 8.52 | 0.93729 | 31.7 | 0.81701 | 270 | 9.137 | 37.68 | 8.682 | 0.9502 | 30.43 | 0.80759 | 264.2 | 76.7 | 25.3 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 15:54 | PSEL | FLI Proline |  |  |  |  | 7.323 | 38.914 | 38.4 | 1.83 | 34.786 | 204.6 |  |  |  |  | 2.36 | 2021-03-02 |  | 2021-03-02 |  | PSEL | ./EL/4181_15_3_02032021_80.tiff | ./EL/4181_15_3_02032021_20.tiff | ./IV/4181_15_3_02012021.csv | 0 | 1 | 2 | ./RefIV/4181_15_3_02012021.csv | 8.862 | 8.862 | 8/30/2018 | 16:19 | 1.0138 | 0.98847
94 | 4181 |  | 15 | 3 |  | 16335 |  | multi-Si module |  |  | OE 517 days | 9.09 | 38.8 | 8.52 | 0.93729 | 31.7 | 0.81701 | 270 | 9.2 | 37.83 | 8.741 | 0.95011 | 30.68 | 0.811 | 268.1 | 77.1 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 9:50 | PSEL | FLI Proline |  |  |  |  | 7.363 | 39.515 | 38.4 | 1.84 | 35.387 | 204.6 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4181_15_3_01302020_80.tiff | ./EL/4181_15_3_01302020_20.tiff | ./IV/4181_15_3_01292020.csv | 0 | 0 | 2 | ./RefIV/4181_15_3_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 16:19 | 1.0137 | 0.99264
95 | 4182 |  | 15 | 3 |  | 16335 |  | multi-Si module |  |  | OE 886 days | 9.09 | 38.8 | 8.52 | 0.93729 | 31.7 | 0.81701 | 270 | 9.169 | 37.76 | 8.701 | 0.94896 | 30.53 | 0.80853 | 265.6 | 76.7 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 15:44 | PSEL | FLI Proline |  |  |  |  | 7.323 | 39.102 | 38.4 | 1.835 | 34.899 | 204.6 |  |  |  |  | 2.36 | 2021-03-02 |  | 2021-03-02 |  | PSEL | ./EL/4182_15_3_02032021_80.tiff | ./EL/4182_15_3_02032021_20.tiff | ./IV/4182_15_3_02012021.csv | 0 | 1 | 2 | ./RefIV/4182_15_3_02012021.csv | 8.862 | 8.862 | 8/30/2018 | 16:23 | 1.0124 | 0.98962
96 | 4182 |  | 15 | 3 |  | 16335 |  | multi-Si module |  |  | OE 517 days | 9.09 | 38.8 | 8.52 | 0.93729 | 31.7 | 0.81701 | 270 | 9.211 | 37.85 | 8.739 | 0.94876 | 30.76 | 0.81268 | 268.8 | 77.1 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 9:51 | PSEL | FLI Proline |  |  |  |  | 7.363 | 39.14 | 38.4 | 1.845 | 35.236 | 204.6 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4182_15_3_01302020_80.tiff | ./EL/4182_15_3_01302020_20.tiff | ./IV/4182_15_3_01292020.csv | 0 | 0 | 2 | ./RefIV/4182_15_3_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 16:23 | 1.0122 | 0.9947
97 | 4179 |  | 15 | 3 |  | 16335 |  | multi-Si module |  |  | OE 886 days | 9.09 | 38.8 | 8.52 | 0.93729 | 31.7 | 0.81701 | 270 | 9.137 | 37.69 | 8.689 | 0.95097 | 30.44 | 0.80764 | 264.5 | 76.8 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 15:51 | PSEL | FLI Proline |  |  |  |  | 7.323 | 38.839 | 38.4 | 1.83 | 34.711 | 150.6 |  |  |  |  | 2.36 | 2021-03-02 |  | 2021-03-02 |  | PSEL | ./EL/4179_15_3_02032021_80.tiff | ./EL/4179_15_3_02032021_20.tiff | ./IV/4179_15_3_02012021.csv | 0 | 1 | 2 | ./RefIV/4179_15_3_02012021.csv | 8.862 | 8.862 | 8/30/2018 | 16:14 | 1.0146 | 0.98853
98 | 4179 |  | 15 | 3 |  | 16335 |  | multi-Si module |  |  | OE 517 days | 9.09 | 38.8 | 8.52 | 0.93729 | 31.7 | 0.81701 | 270 | 9.209 | 37.84 | 8.75 | 0.95016 | 30.66 | 0.81025 | 268.3 | 77 | 25.2 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 9:47 | PSEL | FLI Proline |  |  |  |  | 7.368 | 35.94 | 3.41 | [7 empty] | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4179_15_3_01302020_80.tiff |  | ./IV/4179_15_3_01292020.csv | 0 | 0 | 2 | ./RefIV/4179_15_3_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 16:14 | 1.0137 | 0.99173
99 | 4177 |  | 15 | 3 |  | 16335 |  | multi-Si module |  |  | OE 886 days | 9.09 | 38.8 | 8.52 | 0.93729 | 31.7 | 0.81701 | 270 | 9.166 | 37.78 | 8.702 | 0.94938 | 30.56 | 0.80889 | 265.9 | 76.8 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 15:50 | PSEL | FLI Proline |  |  |  |  | 7.328 | 38.99 | 38.4 | 1.83 | 34.748 | 204.6 |  |  |  |  | 2.36 | 2021-03-02 |  | 2021-03-02 |  | PSEL | ./EL/4177_15_3_02032021_80.tiff | ./EL/4177_15_3_02032021_20.tiff | ./IV/4177_15_3_02012021.csv | 0 | 1 | 2 | ./RefIV/4177_15_3_02012021.csv | 8.862 | 8.862 | 8/30/2018 | 16:06 | 1.0129 | 0.99007
100 | 4177 |  | 15 | 3 |  | 16335 |  | multi-Si module |  |  | OE 517 days | 9.09 | 38.8 | 8.52 | 0.93729 | 31.7 | 0.81701 | 270 | 9.21 | 37.9 | 8.751 | 0.95016 | 30.59 | 0.80712 | 267.7 | 76.7 | 25 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 9:46 | PSEL | FLI Proline |  |  |  |  | 7.368 | 39.59 | 38.4 | 1.84 | 35.387 | 204.6 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4177_15_3_01302020_80.tiff | ./EL/4177_15_3_01302020_20.tiff | ./IV/4177_15_3_01292020.csv | 0 | 0 | 2 | ./RefIV/4177_15_3_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 16:06 | 1.0137 | 0.9879
101 | 3555 |  | 15 | 1 |  | 16344.9 |  | multi-Si module |  |  | OE 1575 days | 8.98 | 38.1 | 8.37 | 0.93207 | 31.1 | 0.81627 | 260 | 8.911 | 37.09 | 8.38 | 0.94041 | 30.04 | 0.80992 | 251.7 | 76.2 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2021-10-02 | 11:27 | PSEL | FLI Proline |  |  |  |  | 7 | 38.4 | 76.8 | 1.6 | 334.9 | 307.2 |  |  |  |  | 2.36 | 2/18/2021 |  | 2/18/2021 |  | PSEL | ./EL/3555_15_1_02182021_80.tiff | ./EL/3555_15_1_02182021_20.tiff | ./IV/3555_15_1_02102021.csv | 0 | 1 | 3 | ./RefIV/3555_15_1_02102021.csv | 8.862 |  | 10/19/2016 | 14:20 | 1.0089 | 0.99222
102 | 3555 |  | 15 | 1 |  | 16344.9 |  | multi-Si module |  |  | OE 223 days | 8.98 | 38.1 | 8.37 | 0.93207 | 31.1 | 0.81627 | 260 | 8.749 | 37.29 | 8.223 | 0.93988 | 30.53 | 0.81872 | 251 | 76.9 | 24.9 | back of panel |  | SPIRE | 4600SLP | 5/30/2017 | 13:51 | PSEL | FLI Proline |  |  |  |  | 7.129 | 37.638 | 76.8 | [7 empty] | 2.36 | 5/30/2017 |  |  |  | PSEL | ./EL/3555_15_1_05302017_80.tiff |  | ./IV/3555_15_1_05302017.csv | 0 | 2 | 3 | ./RefIV/3555_15_1_05302017.csv | 8.714 |  | 10/19/2016 | 14:20 | 1.0084 | 1.003
103 | 3555 |  | 15 | 1 |  | 16351.5 |  | multi-Si module |  |  | OE 1183 days | 8.98 | 38.1 | 8.37 | 0.93207 | 31.1 | 0.81627 | 260 | 8.905 | 37.13 | 8.366 | 0.93947 | 30.28 | 0.81551 | 253.4 | 76.6 | 24.8 | back of panel |  | SPIRE | 4600SLP | 1/15/2020 | 14:00 | PSEL | FLI Proline |  |  |  |  | 7.009 | 38.126 | 76.8 | 1.605 | 33.885 | 307.2 |  |  |  |  | 2.36 | 1/14/2020 |  | 1/14/2020 |  | PSEL | ./EL/3555_15_1_01142020_80.tiff | ./EL/3555_15_1_01142020_20.tiff | ./IV/3555_15_1_01152020.csv | 0 | 0 | 3 | ./RefIV/3555_15_1_01152020.csv | 8.862 |  | 10/19/2016 | 14:20 | 1.0079 | 0.99907
104 | 3538 |  | 15 | 1 |  | 16344.9 |  | multi-Si module |  |  | OE 1575 days | 8.98 | 38.1 | 8.37 | 0.93207 | 31.1 | 0.81627 | 260 | 9.043 | 37.4 | 8.567 | 0.94736 | 30.29 | 0.80989 | 259.5 | 76.7 | 24.6 | back of panel |  | SPIRE | 4600SLP | 2021-10-02 | 11:31 | PSEL | FLI Proline |  |  |  |  | 7.2 | 38.5 | 76.8 | 1.9 | 35.1 | 307.2 |  |  |  |  | 2.36 | 2/18/2021 |  | 2/18/2021 |  | PSEL | ./EL/3538_15_1_02182021_80.tiff | ./EL/3538_15_1_02182021_20.tiff | ./IV/3538_15_1_02102021.csv | 0 | 1 | 2 | ./RefIV/3538_15_1_02102021.csv | 8.862 |  | 10/19/2016 | 16:00 | 1.0164 | 0.99218
105 | 3538 |  | 15 | 1 |  | 16351.5 |  | multi-Si module |  |  | OE 1183 days | 8.98 | 38.1 | 8.37 | 0.93207 | 31.1 | 0.81627 | 260 | 9.053 | 37.5 | 8.581 | 0.94786 | 30.57 | 0.8152 | 262.3 | 77.3 | 24.8 | back of panel |  | SPIRE | 4600SLP | 1/15/2020 | 14:02 | PSEL | FLI Proline |  |  |  |  | 7.009 | 39.539 | 76.8 | 1.605 | 34.411 | 307.2 |  |  |  |  | 2.36 | 1/14/2020 |  | 1/14/2020 |  | PSEL | ./EL/3538_15_1_01142020_80.tiff | ./EL/3538_15_1_01142020_20.tiff | ./IV/3538_15_1_01152020.csv | 0 | 0 | 2 | ./RefIV/3538_15_1_01152020.csv | 8.862 |  | 10/19/2016 | 16:00 | 1.0169 | 0.99869
106 | 3545 |  | 15 | 1 |  | 16344.9 |  | multi-Si module |  |  | OE 1575 days | 8.98 | 38.1 | 8.37 | 0.93207 | 31.1 | 0.81627 | 260 | 9.002 | 37.41 | 8.519 | 0.94635 | 30.27 | 0.80914 | 257.9 | 76.6 | 24.7 | back of panel |  | SPIRE | 4600SLP | 2021-10-02 | 11:28 | PSEL | FLI Proline |  |  |  |  | 7 | 38.5 | 76.8 | 1.6 | 334.9 | 307.2 |  |  |  |  | 2.36 | 2/18/2021 |  | 2/18/2021 |  | PSEL | ./EL/3545_15_1_02182021_80.tiff | ./EL/3545_15_1_02182021_20.tiff | ./IV/3545_15_1_02102021.csv | 0 | 1 | 2 | ./RefIV/3545_15_1_02102021.csv | 8.862 |  | 10/19/2016 | 15:25 | 1.0153 | 0.99126
107 | 3545 |  | 15 | 1 |  | 16351.5 |  | multi-Si module |  |  | OE 1183 days | 8.98 | 38.1 | 8.37 | 0.93207 | 31.1 | 0.81627 | 260 | 9.066 | 37.56 | 8.555 | 0.94364 | 30.66 | 0.81629 | 262.3 | 77 | 24.7 | back of panel |  | SPIRE | 4600SLP | 1/15/2020 | 13:57 | PSEL | FLI Proline |  |  |  |  | 7.009 | 38.652 | 76.8 | 1.605 | 34.448 | 307.2 |  |  |  |  | 2.36 | 1/14/2020 |  | 1/14/2020 |  | PSEL | ./EL/3545_15_1_01142020_80.tiff | ./EL/3545_15_1_01142020_20.tiff | ./IV/3545_15_1_01152020.csv | 0 | 0 | 2 | ./RefIV/3545_15_1_01152020.csv | 8.862 |  | 10/19/2016 | 15:25 | 1.0124 | 1
108 | 3536 |  | 15 | 1 |  | 16344.9 |  | multi-Si module |  |  | OE 1575 days | 8.98 | 38.1 | 8.37 | 0.93207 | 31.1 | 0.81627 | 260 | 8.858 | 37.04 | 8.384 | 0.94649 | 29.94 | 0.80832 | 251 | 76.5 | 25 | back of panel |  | SPIRE | 4600SLP | 2021-10-02 | 11:14 | PSEL | FLI Proline |  |  |  |  | 7 | 38.1 | 76.8 | 1.6 | 35.1 | 307.2 |  |  |  |  | 2.36 | 2/18/2021 |  | 2/18/2021 |  | PSEL | ./EL/3536_15_1_02182021_80.tiff | ./EL/3536_15_1_02182021_20.tiff | ./IV/3536_15_1_02102021.csv | 0 | 0 | 1 | ./RefIV/3536_15_1_02102021.csv | 8.862 |  | 10/19/2016 | 16:39 | 1.0155 | 0.99025
109 | 3534 |  | 15 | 1 |  | 16344.9 |  | multi-Si module |  |  | OE 1575 days | 8.98 | 38.1 | 8.37 | 0.93207 | 31.1 | 0.81627 | 260 | 8.964 | 37.3 | 8.472 | 0.94511 | 30.15 | 0.80831 | 255.5 | 76.4 | 24.6 | back of panel |  | SPIRE | 4600SLP | 2021-10-02 | 11:30 | PSEL | FLI Proline |  |  |  |  | 7 | 38.4 | 76.8 | 1.6 | 35.2 | 307.2 |  |  |  |  | 2.36 | 2/18/2021 |  | 2/18/2021 |  | PSEL | ./EL/3534_15_1_02182021_80.tiff | ./EL/3534_15_1_02182021_20.tiff | ./IV/3534_15_1_02102021.csv | 0 | 1 | 2 | ./RefIV/3534_15_1_02102021.csv | 8.862 |  | 10/19/2016 | 16:34 | 1.014 | 0.99025
110 | 3534 |  | 15 | 1 |  | 16351.5 |  | multi-Si module |  |  | OE 1183 days | 8.98 | 38.1 | 8.37 | 0.93207 | 31.1 | 0.81627 | 260 | 9.028 | 37.56 | 8.555 | 0.94761 | 30.59 | 0.81443 | 261.7 | 77.2 | 24.8 | back of panel |  | SPIRE | 4600SLP | 1/15/2020 | 14:05 | PSEL | FLI Proline |  |  |  |  | 7.009 | 38.689 | 76.8 | 1.605 | 34.523 | 307.2 |  |  |  |  | 2.36 | 1/14/2020 |  | 1/14/2020 |  | PSEL | ./EL/3534_15_1_01142020_80.tiff | ./EL/3534_15_1_01142020_20.tiff | ./IV/3534_15_1_01152020.csv | 0 | 0 | 2 | ./RefIV/3534_15_1_01152020.csv | 8.862 |  | 10/19/2016 | 16:34 | 1.0167 | 0.99774
111 | 3298 |  | 15 | 2 |  | 16351.5 |  | multi-Si module |  |  | OE 1183 days | 9.03 | 38.6 | 8.44 | 0.93466 | 31.4 | 0.81347 | 265 | 9.121 | 37.76 | 8.637 | 0.94694 | 30.24 | 0.80085 | 261.2 | 75.8 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/15/2020 | 13:12 | PSEL | FLI Proline |  |  |  |  | 7.014 | 39.177 | 76.8 | 1.605 | 34.673 | 307.2 |  |  |  |  | 2.36 | 1/14/2020 |  | 1/14/2020 |  | PSEL | ./EL/3298_15_2_01142020_80.tiff | ./EL/3298_15_2_01142020_20.tiff | ./IV/3298_15_2_01152020.csv | 0 | 0 | 1 | ./RefIV/3298_15_2_01152020.csv | 8.862 |  | 10/19/2016 | 12:17 | 1.0131 | 0.98448
112 | 3286 |  | 15 | 2 |  | 16344.9 |  | multi-Si module |  |  | OE 1575 days | 9.03 | 38.6 | 8.44 | 0.93466 | 31.4 | 0.81347 | 265 | 9.148 | 37.73 | 8.651 | 0.94567 | 30.48 | 0.80785 | 263.7 | 76.4 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-10-02 | 11:17 | PSEL | FLI Proline |  |  |  |  | 7.2 | 38.4 | 76.8 | 1.8 | 34.47 | 307.2 |  |  |  |  | 2.36 | 2/18/2021 |  | 2/18/2021 |  | PSEL | ./EL/3286_15_2_02182021_80.tiff | ./EL/3286_15_2_02182021_20.tiff | ./IV/3286_15_2_02102021.csv | 0 | 0 | 1 | ./RefIV/3286_15_2_02102021.csv | 8.862 |  | 10/19/2016 | 11:21 | 1.0118 | 0.99308
113 | 10209 |  | 15 | 2 |  | 16351.5 |  | multi-Si module |  |  | OE 1183 days | 9.03 | 38.6 | 8.44 | 0.93466 | 31.4 | 0.81347 | 265 | 9.154 | 37.8 | 8.637 | 0.94352 | 30.44 | 0.80529 | 262.9 | 76 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/15/2020 | 13:07 | PSEL | FLI Proline |  |  |  |  | 7.009 | 39.102 | 76.8 | 1.61 | 34.786 | 307.2 |  |  |  |  | 2.36 | 1/14/2020 |  | 1/14/2020 |  | PSEL | ./EL/10209_15_2_01142020_80.tiff | ./EL/10209_15_2_01142020_20.tiff | ./IV/10209_15_2_01152020.csv | 0 | 0 | 1 | ./RefIV/10209_15_2_01152020.csv | 8.862 |  | 10/19/2016 | 12:50 | 1.0095 | 0.98994
114 | 3558 |  | 15 | 1 |  | 16344.9 |  | multi-Si module |  |  | OE 1575 days | 8.98 | 38.1 | 8.37 | 0.93207 | 31.1 | 0.81627 | 260 | 8.819 | 36.96 | 8.389 | 0.95124 | 29.91 | 0.80925 | 250.9 | 77 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-10-02 | 11:25 | PSEL | FLI Proline |  |  |  |  | 7 | 38.2 | 76.8 | 1.6 | 33.9 | 307.2 |  |  |  |  | 2.36 | 2/18/2021 |  | 2/18/2021 |  | PSEL | ./EL/3558_15_1_02182021_80.tiff | ./EL/3558_15_1_02182021_20.tiff | ./IV/3558_15_1_02102021.csv | 0 | 1 | 2 | ./RefIV/3558_15_1_02102021.csv | 8.862 |  | 10/19/2016 | 14:10 | 1.0206 | 0.9914
115 | 3558 |  | 15 | 1 |  | 16351.5 |  | multi-Si module |  |  | OE 1183 days | 8.98 | 38.1 | 8.37 | 0.93207 | 31.1 | 0.81627 | 260 | 8.811 | 36.97 | 8.388 | 0.95199 | 30.06 | 0.81309 | 252.2 | 77.4 | 25.2 | back of panel |  | SPIRE | 4600SLP | 1/15/2020 | 13:10 | PSEL | FLI Proline |  |  |  |  | 7.009 | 37.188 | 76.8 | 1.6 | 33.285 | 307.2 |  |  |  |  | 2.36 | 1/14/2020 |  | 1/14/2020 |  | PSEL | ./EL/3558_15_1_01142020_80.tiff | ./EL/3558_15_1_01142020_20.tiff | ./IV/3558_15_1_01152020.csv | 0 | 0 | 2 | ./RefIV/3558_15_1_01152020.csv | 8.862 |  | 10/19/2016 | 14:10 | 1.0214 | 0.9961
116 | 3285 |  | 15 | 2 |  | 16344.9 |  | multi-Si module |  |  | OE 1575 days | 9.03 | 38.6 | 8.44 | 0.93466 | 31.4 | 0.81347 | 265 | 9.178 | 37.82 | 8.7 | 0.94792 | 30.66 | 0.81068 | 266.7 | 76.9 | 25.3 | back of panel |  | SPIRE | 4600SLP | 2021-10-02 | 11:19 | PSEL | FLI Proline |  |  |  |  | 7.1 | 38.8 | 76.8 | 1.8 | 35.1 | 307.2 |  |  |  |  | 2.36 | 2/18/2021 |  | 2/18/2021 |  | PSEL | ./EL/3285_15_2_02182021_80.tiff | ./EL/3285_15_2_02182021_20.tiff | ./IV/3285_15_2_02102021.csv | 0 | 0 | 1 | ./RefIV/3285_15_2_02102021.csv | 8.862 |  | 10/19/2016 | 11:27 | 1.0142 | 0.99657
117 | 3315 |  | 15 | 2 |  | 16344.9 |  | multi-Si module |  |  | OE 1575 days | 9.03 | 38.6 | 8.44 | 0.93466 | 31.4 | 0.81347 | 265 | 9.046 | 37.47 | 8.58 | 0.94849 | 30.32 | 0.80918 | 260.1 | 76.8 | 24.7 | back of panel |  | SPIRE | 4600SLP | 2021-10-02 | 11:36 | PSEL | FLI Proline |  |  |  |  | 7.2 | 38.3 | 76.8 | 1.8 | 34.8 | 307.2 |  |  |  |  | 2.36 | 2/18/2021 |  | 2/18/2021 |  | PSEL | ./EL/3315_15_2_02182021_80.tiff | ./EL/3315_15_2_02182021_20.tiff | ./IV/3315_15_2_02102021.csv | 0 | 1 | 2 | ./RefIV/3315_15_2_02102021.csv | 8.862 |  | 10/19/2016 | 13:07 | 1.0148 | 0.99473
118 | 3315 |  | 15 | 2 |  | 16351.5 |  | multi-Si module |  |  | OE 1183 days | 9.03 | 38.6 | 8.44 | 0.93466 | 31.4 | 0.81347 | 265 | 9.039 | 37.48 | 8.589 | 0.95022 | 30.49 | 0.8135 | 261.9 | 77.3 | 25 | back of panel |  | SPIRE | 4600SLP | 1/15/2020 | 13:02 | PSEL | FLI Proline |  |  |  |  | 7.009 | 38.502 | 76.8 | 1.605 | 34.373 | 307.2 |  |  |  |  | 2.36 | 1/14/2020 |  | 1/14/2020 |  | PSEL | ./EL/3315_15_2_01142020_80.tiff | ./EL/3315_15_2_01142020_20.tiff | ./IV/3315_15_2_01152020.csv | 0 | 0 | 2 | ./RefIV/3315_15_2_01152020.csv | 8.862 |  | 10/19/2016 | 13:07 | 1.0166 | 1
119 | 3280 |  | 15 | 2 |  | 16344.9 |  | multi-Si module |  |  | OE 1575 days | 9.03 | 38.6 | 8.44 | 0.93466 | 31.4 | 0.81347 | 265 | 9.003 | 37.25 | 8.535 | 0.94802 | 30.03 | 0.80617 | 256.3 | 76.4 | 25 | back of panel |  | SPIRE | 4600SLP | 2021-10-02 | 11:39 | PSEL | FLI Proline |  |  |  |  | 7.2 | 38.1 | 76.8 | 1.8 | 34.7 | 307.2 |  |  |  |  | 2.36 | 2/18/2021 |  | 2/18/2021 |  | PSEL | ./EL/3280_15_2_02182021_80.tiff | ./EL/3280_15_2_02182021_20.tiff | ./IV/3280_15_2_02102021.csv | 0 | 1 | 2 | ./RefIV/3280_15_2_02102021.csv | 8.862 |  | 10/19/2016 | 12:00 | 1.0143 | 0.99103
120 | 3280 |  | 15 | 2 |  | 16351.5 |  | multi-Si module |  |  | OE 1183 days | 9.03 | 38.6 | 8.44 | 0.93466 | 31.4 | 0.81347 | 265 | 8.994 | 37.22 | 8.53 | 0.94841 | 30.21 | 0.81166 | 257.7 | 77 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/15/2020 | 13:00 | PSEL | FLI Proline |  |  |  |  | 7.009 | 38.314 | 76.8 | 1.605 | 34.073 | 307.2 |  |  |  |  | 2.36 | 1/14/2020 |  | 1/14/2020 |  | PSEL | ./EL/3280_15_2_01142020_80.tiff | ./EL/3280_15_2_01142020_20.tiff | ./IV/3280_15_2_01152020.csv | 0 | 0 | 2 | ./RefIV/3280_15_2_01152020.csv | 8.862 |  | 10/19/2016 | 12:00 | 1.0147 | 0.99777
121 | 3305 |  | 15 | 2 |  | 16344.9 |  | multi-Si module |  |  | OE 1575 days | 9.03 | 38.6 | 8.44 | 0.93466 | 31.4 | 0.81347 | 265 | 9.014 | 37.3 | 8.561 | 0.94974 | 29.97 | 0.80349 | 256.6 | 76.3 | 24.6 | back of panel |  | SPIRE | 4600SLP | 2021-10-02 | 11:33 | PSEL | FLI Proline |  |  |  |  | 7.2 | 38.5 | 76.8 | 1.9 | 34.7 | 307.2 |  |  |  |  | 2.36 | 2/18/2021 |  | 2/18/2021 |  | PSEL | ./EL/3305_15_2_02182021_80.tiff | ./EL/3305_15_2_02182021_20.tiff | ./IV/3305_15_2_02102021.csv | 0 | 1 | 2 | ./RefIV/3305_15_2_02102021.csv | 8.862 |  | 10/19/2016 | 13:23 | 1.0161 | 0.98772
122 | 3305 |  | 15 | 2 |  | 16351.5 |  | multi-Si module |  |  | OE 1183 days | 9.03 | 38.6 | 8.44 | 0.93466 | 31.4 | 0.81347 | 265 | 8.987 | 37.22 | 8.545 | 0.95082 | 30.12 | 0.80924 | 257.3 | 76.9 | 25.3 | back of panel |  | SPIRE | 4600SLP | 1/15/2020 | 12:56 | PSEL | FLI Proline |  |  |  |  | 7.014 | 38.239 | 76.8 | 1.605 | 34.035 | 307.2 |  |  |  |  | 2.36 | 1/14/2020 |  | 1/14/2020 |  | PSEL | ./EL/3305_15_2_01142020_80.tiff | ./EL/3305_15_2_01142020_20.tiff | ./IV/3305_15_2_01152020.csv | 0 | 0 | 2 | ./RefIV/3305_15_2_01152020.csv | 8.862 |  | 10/19/2016 | 13:23 | 1.0173 | 0.9948
123 | 3548 |  | 15 | 1 |  | 16344.9 |  | multi-Si module |  |  | OE 1575 days | 8.98 | 38.1 | 8.37 | 0.93207 | 31.1 | 0.81627 | 260 | 8.935 | 37.09 | 8.411 | 0.94135 | 30.06 | 0.81046 | 252.8 | 76.3 | 25.4 | back of panel |  | SPIRE | 4600SLP | 2021-10-02 | 11:21 | PSEL | FLI Proline |  |  |  |  | 7 | 38 | 76.8 | 1.6 | 34 | 307.2 |  |  |  |  | 2.36 | 2/18/2021 |  | 2/18/2021 |  | PSEL | ./EL/3548_15_1_02182021_80.tiff | ./EL/3548_15_1_02182021_20.tiff | ./IV/3548_15_1_02102021.csv | 0 | 0 | 1 | ./RefIV/3548_15_1_02102021.csv | 8.862 |  | 10/19/2016 | 14:43 | 1.01 | 0.99288
124 | 3549 |  | 15 | 1 |  | 16344.9 |  | multi-Si module |  |  | OE 1575 days | 8.98 | 38.1 | 8.37 | 0.93207 | 31.1 | 0.81627 | 260 | 8.822 | 36.96 | 8.369 | 0.94865 | 29.91 | 0.80925 | 250.3 | 76.8 | 25.3 | back of panel |  | SPIRE | 4600SLP | 2021-10-02 | 11:24 | PSEL | FLI Proline |  |  |  |  | 7 | 38.3 | 76.8 | 1.6 | 34 | 307.2 |  |  |  |  | 2.36 | 2/18/2021 |  | 2/18/2021 |  | PSEL | ./EL/3549_15_1_02182021_80.tiff | ./EL/3549_15_1_02182021_20.tiff | ./IV/3549_15_1_02102021.csv | 0 | 1 | 2 | ./RefIV/3549_15_1_02102021.csv | 8.862 |  | 10/19/2016 | 14:39 | 1.0178 | 0.9914
125 | 3549 |  | 15 | 1 |  | 16351.5 |  | multi-Si module |  |  | OE 1183 days | 8.98 | 38.1 | 8.37 | 0.93207 | 31.1 | 0.81627 | 260 | 8.842 | 36.95 | 8.37 | 0.94662 | 30.03 | 0.81272 | 251.3 | 76.9 | 25.2 | back of panel |  | SPIRE | 4600SLP | 1/15/2020 | 13:32 | PSEL | FLI Proline |  |  |  |  | 7.014 | 37.976 | 76.8 | 1.605 | 33.66 | 307.2 |  |  |  |  | 2.36 | 1/14/2020 |  | 1/14/2020 |  | PSEL | ./EL/3549_15_1_01142020_80.tiff | ./EL/3549_15_1_01142020_20.tiff | ./IV/3549_15_1_01152020.csv | 0 | 0 | 2 | ./RefIV/3549_15_1_01152020.csv | 8.862 |  | 10/19/2016 | 14:39 | 1.0156 | 0.99565
126 | 3554 |  | 15 | 1 |  | 16344.9 |  | multi-Si module |  |  | OE 1575 days | 8.98 | 38.1 | 8.37 | 0.93207 | 31.1 | 0.81627 | 260 | 8.876 | 37 | 8.368 | 0.94277 | 29.99 | 0.81054 | 250.9 | 76.4 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2021-10-02 | 11:26 | PSEL | FLI Proline |  |  |  |  | 7 | 38 | 76.8 | 1.6 | 34.1 | 307.2 |  |  |  |  | 2.36 | 2/18/2021 |  | 2/18/2021 |  | PSEL | ./EL/3554_15_1_02182021_80.tiff | ./EL/3554_15_1_02182021_20.tiff | ./IV/3554_15_1_02102021.csv | 0 | 0 | 1 | ./RefIV/3554_15_1_02102021.csv | 8.862 |  | 10/19/2016 | 14:23 | 1.0115 | 0.99298
127 | 3311 |  | 15 | 2 |  | 16344.9 |  | multi-Si module |  |  | OE 1575 days | 9.03 | 38.6 | 8.44 | 0.93466 | 31.4 | 0.81347 | 265 | 8.993 | 37.37 | 8.561 | 0.95196 | 30.21 | 0.8084 | 258.6 | 77 | 24.7 | back of panel |  | SPIRE | 4600SLP | 2021-10-02 | 11:34 | PSEL | FLI Proline | [7 empty] | 1.8 | 34.9 | 76.8 |  |  |  |  | 2.36 | 2/18/2021 |  | 2/18/2021 |  | PSEL |  | ./EL/3311_15_2_02182021_20.tiff | ./IV/3311_15_2_02102021.csv | 0 | 1 | 2 | ./RefIV/3311_15_2_02102021.csv | 8.862 |  | 10/19/2016 | 12:54 | 1.0185 | 0.99377
128 | 3311 |  | 15 | 2 |  | 16351.5 |  | multi-Si module |  |  | OE 1183 days | 9.03 | 38.6 | 8.44 | 0.93466 | 31.4 | 0.81347 | 265 | 8.998 | 37.37 | 8.569 | 0.95232 | 30.39 | 0.81322 | 260.5 | 77.5 | 25.2 | back of panel |  | SPIRE | 4600SLP | 1/15/2020 | 13:05 | PSEL | FLI Proline |  |  |  |  | 7.009 | 38.389 | 76.8 | 1.605 | 34.298 | 307.2 |  |  |  |  | 2.36 | 1/14/2020 |  | 1/14/2020 |  | PSEL | ./EL/3311_15_2_01142020_80.tiff | ./EL/3311_15_2_01142020_20.tiff | ./IV/3311_15_2_01152020.csv | 0 | 0 | 2 | ./RefIV/3311_15_2_01152020.csv | 8.862 |  | 10/19/2016 | 12:54 | 1.0189 | 0.99969
129 | 3547 |  | 15 | 1 |  | 16351.5 |  | multi-Si module |  |  | OE 1183 days | 8.98 | 38.1 | 8.37 | 0.93207 | 31.1 | 0.81627 | 260 | 8.798 | 36.94 | 8.348 | 0.94885 | 30.03 | 0.81294 | 250.7 | 77.2 | 25.2 | back of panel |  | SPIRE | 4600SLP | 1/15/2020 | 13:25 | PSEL | FLI Proline |  |  |  |  | 7.009 | 37.976 | 76.8 | 1.605 | 33.623 | 307.2 |  |  |  |  | 2.36 | 1/14/2020 |  | 1/14/2020 |  | PSEL | ./EL/3547_15_1_01142020_80.tiff | ./EL/3547_15_1_01142020_20.tiff | ./IV/3547_15_1_01152020.csv | 0 | 0 | 1 | ./RefIV/3547_15_1_01152020.csv | 8.862 |  | 10/19/2016 | 14:50 | 1.018 | 0.99592
130 | 3551 |  | 15 | 1 |  | 16351.5 |  | multi-Si module |  |  | OE 1183 days | 8.98 | 38.1 | 8.37 | 0.93207 | 31.1 | 0.81627 | 260 | 8.934 | 37.07 | 8.345 | 0.93407 | 30.27 | 0.81656 | 252.6 | 76.3 | 24.7 | back of panel |  | SPIRE | 4600SLP | 1/15/2020 | 13:53 | PSEL | FLI Proline |  |  |  |  | 7.009 | 37.939 | 76.8 | 1.605 | 33.735 | 307.2 |  |  |  |  | 2.36 | 1/14/2020 |  | 1/14/2020 |  | PSEL | ./EL/3551_15_1_01142020_80.tiff | ./EL/3551_15_1_01142020_20.tiff | ./IV/3551_15_1_01152020.csv | 0 | 0 | 1 | ./RefIV/3551_15_1_01152020.csv | 8.862 |  | 10/19/2016 | 14:31 | 1.0021 | 1.0004
131 | 4180 |  | 15 | 3 |  | 16335 |  | multi-Si module |  |  | OE 517 days | 9.09 | 38.8 | 8.52 | 0.93729 | 31.7 | 0.81701 | 270 | 9.143 | 37.79 | 8.703 | 0.95188 | 30.6 | 0.80974 | 266.3 | 77.1 | 25 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 9:48 | PSEL | FLI Proline |  |  |  |  | 7.363 | 39.365 | 38.4 | 1.84 | 35.161 | 204.6 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4180_15_3_01302020_80.tiff | ./EL/4180_15_3_01302020_20.tiff | ./IV/4180_15_3_01292020.csv | 0 | 0 | 1 | ./RefIV/4180_15_3_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 16:17 | 1.0156 | 0.9911
132 | 4188 |  | 22 | 4 |  | 16742.7 |  | mono-Si module |  |  | OE 0 days | 6.07 | 69.7 | 5.7 | 0.93904 | 58 | 0.83214 | 330 | 5.981 | 70.4 | 5.623 | 0.94014 | 58.66 | 0.83324 | 329.8 | 78.3 | 24.8 | back of panel |  | SPIRE | 4600SLP | 9/14/2018 | 9:48 | PSEL | FLI Proline |  |  |  |  | 4.821 | 73.468 | 0.6 | 1.206 | 66.613 | 2.4 |  |  |  |  | 2.36 | 9/14/2018 |  | 9/14/2018 |  | PSEL | ./EL/4188_22_4_09142018_80.tiff | ./EL/4188_22_4_09142018_20.tiff | ./IV/4188_22_4_09142018.csv | 0 | 1 | 2 | ./RefIV/4188_22_4_09142018.csv | 8.862 | 8.862 | 9/14/2018 | 9:48 | 1.0012 | 1.0013
133 | 4188 |  | 22 | 4 |  | 16742.7 |  | mono-Si module |  |  | OE 871 days | 6.07 | 69.7 | 5.7 | 0.93904 | 58 | 0.83214 | 330 | 5.999 | 69.87 | 5.648 | 0.94149 | 58.05 | 0.83083 | 327.9 | 78.2 | 24.8 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 16:20 | PSEL | FLI Proline |  |  |  |  | 4.816 | 72.017 | 0.6 | 1.206 | 65.937 | 2.4 |  |  |  |  | 2.36 | 2021-02-02 |  | 2021-02-02 |  | PSEL | ./EL/4188_22_4_02022021_80.tiff | ./EL/4188_22_4_02022021_20.tiff | ./IV/4188_22_4_02012021.csv | 0 | 0 | 2 | ./RefIV/4188_22_4_02012021.csv | 8.862 | 8.862 | 9/14/2018 | 9:48 | 1.0026 | 0.99843
134 | 4190 |  | 22 | 4 |  | 16742.7 |  | mono-Si module |  |  | OE 0 days | 6.07 | 69.7 | 5.7 | 0.93904 | 58 | 0.83214 | 330 | 5.997 | 70.53 | 5.618 | 0.9368 | 58.62 | 0.83114 | 329.4 | 77.9 | 25.3 | back of panel |  | SPIRE | 4600SLP | 9/14/2018 | 9:57 | PSEL | FLI Proline |  |  |  |  | 4.821 | 73.218 | 0.6 | 1.206 | 67.213 | 2.4 |  |  |  |  | 2.36 | 9/14/2018 |  | 9/14/2018 |  | PSEL | ./EL/4190_22_4_09142018_80.tiff | ./EL/4190_22_4_09142018_20.tiff | ./IV/4190_22_4_09142018.csv | 0 | 0 | 1 | ./RefIV/4190_22_4_09142018.csv | 8.862 | 8.862 | 9/14/2018 | 9:57 | 0.99761 | 0.9988
135 | 4194 |  | 22 | 4 |  | 16742.7 |  | mono-Si module |  |  | OE 0 days | 6.07 | 69.7 | 5.7 | 0.93904 | 58 | 0.83214 | 330 | 6.002 | 70.6 | 5.621 | 0.93652 | 58.64 | 0.83059 | 329.6 | 77.8 | 24.9 | back of panel |  | SPIRE | 4600SLP | 9/14/2018 | 10:47 | PSEL | FLI Proline |  |  |  |  | 4.821 | 73.068 | 0.8 | 1.206 | 67.025 | 2.4 |  |  |  |  | 2.36 | 9/14/2018 |  | 9/14/2018 |  | PSEL | ./EL/4194_22_4_09142018_80.tiff | ./EL/4194_22_4_09142018_20.tiff | ./IV/4194_22_4_09142018.csv | 0 | 1 | 2 | ./RefIV/4194_22_4_09142018.csv | 8.862 | 8.862 | 9/14/2018 | 10:47 | 0.99731 | 0.99815
136 | 4194 |  | 22 | 4 |  | 16742.7 |  | mono-Si module |  |  | OE 871 days | 6.07 | 69.7 | 5.7 | 0.93904 | 58 | 0.83214 | 330 | 6.013 | 70.08 | 5.65 | 0.93963 | 58.08 | 0.82877 | 328.2 | 77.9 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 16:12 | PSEL | FLI Proline |  |  |  |  | 4.816 | 72.242 | 0.6 | 1.206 | 66.312 | 2.4 |  |  |  |  | 2.36 | 2021-02-02 |  | 2021-02-02 |  | PSEL | ./EL/4194_22_4_02022021_80.tiff | ./EL/4194_22_4_02022021_20.tiff | ./IV/4194_22_4_02012021.csv | 0 | 0 | 2 | ./RefIV/4194_22_4_02012021.csv | 8.862 | 8.862 | 9/14/2018 | 10:47 | 1.0006 | 0.99595
137 | 4186 |  | 22 | 4 |  | 16742.7 |  | mono-Si module |  |  | OE 0 days | 6.07 | 69.7 | 5.7 | 0.93904 | 58 | 0.83214 | 330 | 6.006 | 70.47 | 5.625 | 0.93656 | 58.63 | 0.83199 | 329.8 | 77.9 | 25 | back of panel |  | SPIRE | 4600SLP | 9/14/2018 | 9:42 | PSEL | FLI Proline |  |  |  |  | 4.821 | 73.068 | 0.6 | 1.206 | 67.101 | 2.4 |  |  |  |  | 2.36 | 9/14/2018 |  | 9/14/2018 |  | PSEL | ./EL/4186_22_4_09142018_80.tiff | ./EL/4186_22_4_09142018_20.tiff | ./IV/4186_22_4_09142018.csv | 0 | 1 | 2 | ./RefIV/4186_22_4_09142018.csv | 8.862 | 8.862 | 9/14/2018 | 9:42 | 0.99736 | 0.99982
138 | 4186 |  | 22 | 4 |  | 16742.7 |  | mono-Si module |  |  | OE 871 days | 6.07 | 69.7 | 5.7 | 0.93904 | 58 | 0.83214 | 330 | 6.018 | 70.03 | 5.648 | 0.93852 | 58.11 | 0.82979 | 328.2 | 77.9 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 16:21 | PSEL | FLI Proline |  |  |  |  | 4.816 | 72.167 | 0.6 | 1.206 | 66.35 | 2.4 |  |  |  |  | 2.36 | 2021-02-02 |  | 2021-02-02 |  | PSEL | ./EL/4186_22_4_02022021_80.tiff | ./EL/4186_22_4_02022021_20.tiff | ./IV/4186_22_4_02012021.csv | 0 | 0 | 2 | ./RefIV/4186_22_4_02012021.csv | 8.862 | 8.862 | 9/14/2018 | 9:42 | 0.99944 | 0.99718
139 | 4185 |  | 22 | 4 |  | 16742.7 |  | mono-Si module |  |  | OE 0 days | 6.07 | 69.7 | 5.7 | 0.93904 | 58 | 0.83214 | 330 | 6.006 | 70.58 | 5.622 | 0.93606 | 58.65 | 0.83097 | 329.8 | 77.8 | 25.3 | back of panel |  | SPIRE | 4600SLP | 9/14/2018 | 9:29 | PSEL | FLI Proline |  |  |  |  | 4.821 | 73.218 | 0.6 | 1.211 | 67.288 | 2.4 |  |  |  |  | 2.36 | 9/14/2018 |  | 9/14/2018 |  | PSEL | ./EL/4185_22_4_09142018_80.tiff | ./EL/4185_22_4_09142018_20.tiff | ./IV/4185_22_4_09142018.csv | 0 | 1 | 2 | ./RefIV/4185_22_4_09142018.csv | 8.862 | 8.862 | 9/14/2018 | 9:29 | 0.99683 | 0.9986
140 | 4185 |  | 22 | 4 |  | 16742.7 |  | mono-Si module |  |  | OE 871 days | 6.07 | 69.7 | 5.7 | 0.93904 | 58 | 0.83214 | 330 | 6.018 | 70.12 | 5.652 | 0.93918 | 58.12 | 0.82886 | 328.5 | 77.8 | 25 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 16:14 | PSEL | FLI Proline |  |  |  |  | 4.811 | 72.43 | 0.6 | 1.206 | 66.425 | 2.4 |  |  |  |  | 2.36 | 2021-02-02 |  | 2021-02-02 |  | PSEL | ./EL/4185_22_4_02022021_80.tiff | ./EL/4185_22_4_02022021_20.tiff | ./IV/4185_22_4_02012021.csv | 0 | 0 | 2 | ./RefIV/4185_22_4_02012021.csv | 8.862 | 8.862 | 9/14/2018 | 9:29 | 1.0001 | 0.99607
141 | 4189 |  | 22 | 4 |  | 16742.7 |  | mono-Si module |  |  | OE 0 days | 6.07 | 69.7 | 5.7 | 0.93904 | 58 | 0.83214 | 330 | 6 | 70.34 | 5.62 | 0.93667 | 58.48 | 0.83139 | 328.6 | 77.9 | 25.1 | back of panel |  | SPIRE | 4600SLP | 9/14/2018 | 9:51 | PSEL | FLI Proline |  |  |  |  | 4.811 | 72.843 | 0.6 | 1.206 | 66.875 | 2.4 |  |  |  |  | 2.36 | 9/14/2018 |  | 9/14/2018 |  | PSEL | ./EL/4189_22_4_09142018_80.tiff | ./EL/4189_22_4_09142018_20.tiff | ./IV/4189_22_4_09142018.csv | 0 | 1 | 2 | ./RefIV/4189_22_4_09142018.csv | 8.862 | 8.862 | 9/14/2018 | 9:51 | 0.99747 | 0.9991
142 | 4189 |  | 22 | 4 |  | 16742.7 |  | mono-Si module |  |  | OE 871 days | 6.07 | 69.7 | 5.7 | 0.93904 | 58 | 0.83214 | 330 | 6.021 | 69.73 | 5.649 | 0.93822 | 57.76 | 0.82834 | 326.3 | 77.7 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 16:18 | PSEL | FLI Proline |  |  |  |  | 4.816 | 71.942 | 0.6 | 1.206 | 65.9 | 2.4 |  |  |  |  | 2.36 | 2021-02-02 |  | 2021-02-02 |  | PSEL | ./EL/4189_22_4_02022021_80.tiff | ./EL/4189_22_4_02022021_20.tiff | ./IV/4189_22_4_02012021.csv | 0 | 0 | 2 | ./RefIV/4189_22_4_02012021.csv | 8.862 | 8.862 | 9/14/2018 | 9:51 | 0.99912 | 0.99543
143 | 4191 |  | 22 | 4 |  | 16742.7 |  | mono-Si module |  |  | OE 0 days | 6.07 | 69.7 | 5.7 | 0.93904 | 58 | 0.83214 | 330 | 5.993 | 70.52 | 5.628 | 0.9391 | 58.65 | 0.83168 | 330.1 | 78.1 | 24.9 | back of panel |  | SPIRE | 4600SLP | 9/14/2018 | 10:20 | PSEL | FLI Proline |  |  |  |  | 4.816 | 73.03 | 0.6 | 1.206 | 67.101 | 2.4 |  |  |  |  | 2.36 | 9/14/2018 |  | 9/14/2018 |  | PSEL | ./EL/4191_22_4_09142018_80.tiff | ./EL/4191_22_4_09142018_20.tiff | ./IV/4191_22_4_09142018.csv | 0 | 1 | 2 | ./RefIV/4191_22_4_09142018.csv | 8.862 | 8.862 | 9/14/2018 | 10:20 | 1.0001 | 0.99945
144 | 4191 |  | 22 | 4 |  | 16742.7 |  | mono-Si module |  |  | OE 871 days | 6.07 | 69.7 | 5.7 | 0.93904 | 58 | 0.83214 | 330 | 5.997 | 69.96 | 5.651 | 0.9423 | 58.04 | 0.82962 | 328 | 78.2 | 25.3 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 16:19 | PSEL | FLI Proline |  |  |  |  | 4.816 | 72.055 | 0.6 | 1.211 | 66.125 | 2.4 |  |  |  |  | 2.36 | 2021-02-02 |  | 2021-02-02 |  | PSEL | ./EL/4191_22_4_02022021_80.tiff | ./EL/4191_22_4_02022021_20.tiff | ./IV/4191_22_4_02012021.csv | 0 | 0 | 2 | ./RefIV/4191_22_4_02012021.csv | 8.862 | 8.862 | 9/14/2018 | 10:20 | 1.0035 | 0.99697
145 | 4187 |  | 22 | 4 |  | 16742.7 |  | mono-Si module |  |  | OE 0 days | 6.07 | 69.7 | 5.7 | 0.93904 | 58 | 0.83214 | 330 | 6.011 | 70.54 | 5.621 | 0.93512 | 58.59 | 0.83059 | 329.4 | 77.7 | 25 | back of panel |  | SPIRE | 4600SLP | 9/14/2018 | 9:44 | PSEL | FLI Proline |  |  |  |  | 4.811 | 73.143 | 0.6 | 1.206 | 67.176 | 2.4 |  |  |  |  | 2.36 | 9/14/2018 |  | 9/14/2018 |  | PSEL | ./EL/4187_22_4_09142018_80.tiff | ./EL/4187_22_4_09142018_20.tiff | ./IV/4187_22_4_09142018.csv | 0 | 1 | 2 | ./RefIV/4187_22_4_09142018.csv | 8.862 | 8.862 | 9/14/2018 | 9:44 | 0.99582 | 0.99814
146 | 4187 |  | 22 | 4 |  | 16742.7 |  | mono-Si module |  |  | OE 871 days | 6.07 | 69.7 | 5.7 | 0.93904 | 58 | 0.83214 | 330 | 6.02 | 70.07 | 5.646 | 0.93787 | 58.08 | 0.82889 | 327.9 | 77.7 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 16:17 | PSEL | FLI Proline |  |  |  |  | 4.821 | 72.355 | 0.6 | 1.211 | 66.425 | 2.4 |  |  |  |  | 2.36 | 2021-02-02 |  | 2021-02-02 |  | PSEL | ./EL/4187_22_4_02022021_80.tiff | ./EL/4187_22_4_02022021_20.tiff | ./IV/4187_22_4_02012021.csv | 0 | 0 | 2 | ./RefIV/4187_22_4_02012021.csv | 8.862 | 8.862 | 9/14/2018 | 9:44 | 0.99875 | 0.99609
147 | 4193 |  | 22 | 4 |  | 16742.7 |  | mono-Si module |  |  | OE 0 days | 6.07 | 69.7 | 5.7 | 0.93904 | 58 | 0.83214 | 330 | 5.995 | 70.53 | 5.622 | 0.93778 | 58.69 | 0.83213 | 329.9 | 78 | 25.4 | back of panel |  | SPIRE | 4600SLP | 9/14/2018 | 10:43 | PSEL | FLI Proline |  |  |  |  | 4.816 | 73.218 | 0.8 | 1.206 | 67.101 | 2.4 |  |  |  |  | 2.36 | 9/14/2018 |  | 9/14/2018 |  | PSEL | ./EL/4193_22_4_09142018_80.tiff | ./EL/4193_22_4_09142018_20.tiff | ./IV/4193_22_4_09142018.csv | 0 | 1 | 2 | ./RefIV/4193_22_4_09142018.csv | 8.862 | 8.862 | 9/14/2018 | 10:43 | 0.99866 | 0.99999
148 | 4193 |  | 22 | 4 |  | 16742.7 |  | mono-Si module |  |  | OE 871 days | 6.07 | 69.7 | 5.7 | 0.93904 | 58 | 0.83214 | 330 | 6.015 | 70.1 | 5.645 | 0.93849 | 58.21 | 0.83039 | 328.6 | 77.9 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 16:16 | PSEL | FLI Proline |  |  |  |  | 4.816 | 72.242 | 0.6 | 1.211 | 66.425 | 2.4 |  |  |  |  | 2.36 | 2021-02-02 |  | 2021-02-02 |  | PSEL | ./EL/4193_22_4_02022021_80.tiff | ./EL/4193_22_4_02022021_20.tiff | ./IV/4193_22_4_02012021.csv | 0 | 0 | 2 | ./RefIV/4193_22_4_02012021.csv | 8.862 | 8.862 | 9/14/2018 | 10:43 | 0.99941 | 0.99789
149 | 4192 |  | 22 | 4 |  | 16742.7 |  | mono-Si module |  |  | OE 0 days | 6.07 | 69.7 | 5.7 | 0.93904 | 58 | 0.83214 | 330 | 6.005 | 70.48 | 5.634 | 0.93822 | 58.59 | 0.8313 | 330.1 | 78 | 25.1 | back of panel |  | SPIRE | 4600SLP | 9/14/2018 | 10:23 | PSEL | FLI Proline |  |  |  |  | 4.821 | 73.03 | 0.6 | 1.206 | 66.988 | 2.45 |  |  |  |  | 2.36 | 9/14/2018 |  | 9/14/2018 |  | PSEL | ./EL/4192_22_4_09142018_80.tiff | ./EL/4192_22_4_09142018_20.tiff | ./IV/4192_22_4_09142018.csv | 0 | 1 | 2 | ./RefIV/4192_22_4_09142018.csv | 8.862 | 8.862 | 9/14/2018 | 10:23 | 0.99912 | 0.99899
150 | 4192 |  | 22 | 4 |  | 16742.7 |  | mono-Si module |  |  | OE 871 days | 6.07 | 69.7 | 5.7 | 0.93904 | 58 | 0.83214 | 330 | 6.02 | 69.96 | 5.663 | 0.9407 | 58.01 | 0.82919 | 328.5 | 78 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 16:10 | PSEL | FLI Proline |  |  |  |  | 4.811 | 72.242 | 0.6 | 1.206 | 66.312 | 2.4 |  |  |  |  | 2.36 | 2021-02-02 |  | 2021-02-02 |  | PSEL | ./EL/4192_22_4_02022021_80.tiff | ./EL/4192_22_4_02022021_20.tiff | ./IV/4192_22_4_02012021.csv | 0 | 0 | 2 | ./RefIV/4192_22_4_02012021.csv | 8.862 | 8.862 | 9/14/2018 | 10:23 | 1.0018 | 0.99646
151 | 3844 |  | 22 | 3 |  | 16690 |  | mono-Si module |  |  | OE 740 days | 6.03 | 69.6 | 5.65 | 0.93698 | 57.6 | 0.82759 | 325 | 6.028 | 69.58 | 5.696 | 0.94492 | 57.81 | 0.83084 | 329.3 | 78.5 | 25.4 | back of panel |  | SPIRE | 4600SLP | 1/21/2020 | 10:24 | PSEL | FLI Proline |  |  |  |  | 4.811 | 71.942 | 0.8 | 1.206 | 65.9 | 3.2 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3844_22_3_01172020_80.tiff | ./EL/3844_22_3_01172020_20.tiff | ./IV/3844_22_3_01212020.csv | 0 | 0 | 2 | ./RefIV/3844_22_3_01212020.csv | 8.862 | 9.248 | 2018-11-01 | 16:58 | 1.0085 | 1.0039
152 | 3844 |  | 22 | 3 |  | 16690 |  | mono-Si module |  |  | OE 1112 days | 6.03 | 69.6 | 5.65 | 0.93698 | 57.6 | 0.82759 | 325 | 6.034 | 69.36 | 5.639 | 0.93454 | 57.37 | 0.82713 | 323.5 | 77.3 | 25.2 | back of panel |  | SPIRE | 4600SLP | 1/27/2021 | 15:51 | PSEL | FLI Proline |  |  |  |  | 4.821 | 71.754 | 0.8 | 1.211 | 65.637 | 3.2 |  |  |  |  | 2.36 | 1/29/2021 |  | 1/29/2021 |  | PSEL | ./EL/3844_22_3_01292021_80.tiff | ./EL/3844_22_3_01292021_20.tiff | ./IV/3844_22_3_01272021.csv | 0 | 1 | 2 | ./RefIV/3844_22_3_01272021.csv | 8.862 | 9.248 | 2018-11-01 | 16:58 | 0.99739 | 0.99945
153 | 3845 |  | 22 | 3 |  | 16690 |  | mono-Si module |  |  | OE 740 days | 6.03 | 69.6 | 5.65 | 0.93698 | 57.6 | 0.82759 | 325 | 5.999 | 69.51 | 5.696 | 0.94949 | 57.77 | 0.8311 | 329.1 | 78.9 | 25.3 | back of panel |  | SPIRE | 4600SLP | 1/21/2020 | 10:25 | PSEL | FLI Proline |  |  |  |  | 4.811 | 71.867 | 0.8 | 1.206 | 65.9 | 3.2 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3845_22_3_01172020_80.tiff | ./EL/3845_22_3_01172020_20.tiff | ./IV/3845_22_3_01212020.csv | 0 | 0 | 2 | ./RefIV/3845_22_3_01212020.csv | 8.862 | 9.248 | 2018-11-01 | 17:06 | 1.0134 | 1.0042
154 | 3845 |  | 22 | 3 |  | 16690 |  | mono-Si module |  |  | OE 1112 days | 6.03 | 69.6 | 5.65 | 0.93698 | 57.6 | 0.82759 | 325 | 5.999 | 69.29 | 5.641 | 0.94032 | 57.33 | 0.82739 | 323.4 | 77.8 | 25 | back of panel |  | SPIRE | 4600SLP | 1/27/2021 | 15:53 | PSEL | FLI Proline |  |  |  |  | 4.816 | 71.642 | 0.8 | 1.206 | 65.599 | 3.2 |  |  |  |  | 2.36 | 1/29/2021 |  | 1/29/2021 |  | PSEL | ./EL/3845_22_3_01292021_80.tiff | ./EL/3845_22_3_01292021_20.tiff | ./IV/3845_22_3_01272021.csv | 0 | 1 | 2 | ./RefIV/3845_22_3_01272021.csv | 8.862 | 9.248 | 2018-11-01 | 17:06 | 1.0036 | 0.99977
155 | 3836 |  | 22 | 3 |  | 16690 |  | mono-Si module |  |  | OE 740 days | 6.03 | 69.6 | 5.65 | 0.93698 | 57.6 | 0.82759 | 325 | 6.012 | 69.48 | 5.694 | 0.94711 | 57.68 | 0.83017 | 328.4 | 78.6 | 25.3 | back of panel |  | SPIRE | 4600SLP | 1/21/2020 | 10:13 | PSEL | FLI Proline |  |  |  |  | 4.811 | 71.829 | 0.8 | 1.201 | 65.824 | 3.2 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3836_22_3_01172020_80.tiff | ./EL/3836_22_3_01172020_20.tiff | ./IV/3836_22_3_01212020.csv | 0 | 0 | 2 | ./RefIV/3836_22_3_01212020.csv | 8.862 | 9.248 | 2018-11-01 | 13:06 | 1.0108 | 1.0031
156 | 3836 |  | 22 | 3 |  | 16690 |  | mono-Si module |  |  | OE 1112 days | 6.03 | 69.6 | 5.65 | 0.93698 | 57.6 | 0.82759 | 325 | 6.015 | 69.25 | 5.647 | 0.93882 | 57.2 | 0.82599 | 323 | 77.6 | 25 | back of panel |  | SPIRE | 4600SLP | 1/27/2021 | 16:00 | PSEL | FLI Proline |  |  |  |  | 4.816 | 71.604 | 0.8 | 1.211 | 65.449 | 3.2 |  |  |  |  | 2.36 | 1/29/2021 |  | 1/29/2021 |  | PSEL | ./EL/3836_22_3_01292021_80.tiff | ./EL/3836_22_3_01292021_20.tiff | ./IV/3836_22_3_01272021.csv | 0 | 1 | 2 | ./RefIV/3836_22_3_01272021.csv | 8.862 | 9.248 | 2018-11-01 | 13:06 | 1.002 | 0.99807
157 | 3850 |  | 22 | 3 |  | 16690 |  | mono-Si module |  |  | OE 740 days | 6.03 | 69.6 | 5.65 | 0.93698 | 57.6 | 0.82759 | 325 | 6.005 | 69.58 | 5.697 | 0.94871 | 57.77 | 0.83027 | 329.1 | 78.8 | 25.2 | back of panel |  | SPIRE | 4600SLP | 1/21/2020 | 10:29 | PSEL | FLI Proline |  |  |  |  | 4.816 | 72.242 | 0.8 | 1.201 | 66.2 | 3.2 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3850_22_3_01172020_80.tiff | ./EL/3850_22_3_01172020_20.tiff | ./IV/3850_22_3_01212020.csv | 0 | 0 | 2 | ./RefIV/3850_22_3_01212020.csv | 8.862 | 9.248 | 2018-11-01 | 17:51 | 1.0125 | 1.0032
158 | 3850 |  | 22 | 3 |  | 16690 |  | mono-Si module |  |  | OE 1112 days | 6.03 | 69.6 | 5.65 | 0.93698 | 57.6 | 0.82759 | 325 | 6.009 | 69.28 | 5.635 | 0.93776 | 57.26 | 0.8265 | 322.7 | 77.5 | 25.2 | back of panel |  | SPIRE | 4600SLP | 1/27/2021 | 15:46 | PSEL | FLI Proline |  |  |  |  | 1.211 | 71.642 | 0.8 | 1.211 | 65.562 | 3.2 |  |  |  |  | 2.36 | 1/29/2021 |  | 1/29/2021 |  | PSEL | ./EL/3850_22_3_01292021_80.tiff | ./EL/3850_22_3_01292021_20.tiff | ./IV/3850_22_3_01272021.csv | 0 | 1 | 2 | ./RefIV/3850_22_3_01272021.csv | 8.862 | 9.248 | 2018-11-01 | 17:51 | 1.0008 | 0.99869
159 | 3851 |  | 22 | 3 |  | 16690 |  | mono-Si module |  |  | OE 740 days | 6.03 | 69.6 | 5.65 | 0.93698 | 57.6 | 0.82759 | 325 | 6.009 | 69.42 | 5.698 | 0.94824 | 57.59 | 0.82959 | 328.2 | 78.7 | 25.4 | back of panel |  | SPIRE | 4600SLP | 1/21/2020 | 10:28 | PSEL | FLI Proline | [7 empty] | 1.206 | 65.937 | 3.2 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL |  | ./EL/3851_22_3_01172020_20.tiff | ./IV/3851_22_3_01212020.csv | 0 | 0 | 2 | ./RefIV/3851_22_3_01212020.csv | 8.862 | 9.248 | 2018-11-01 | 17:57 | 1.012 | 1.0024
160 | 3851 |  | 22 | 3 |  | 16690 |  | mono-Si module |  |  | OE 1112 days | 6.03 | 69.6 | 5.65 | 0.93698 | 57.6 | 0.82759 | 325 | 6.005 | 69.13 | 5.633 | 0.93805 | 57.15 | 0.8267 | 321.9 | 77.5 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/27/2021 | 15:48 | PSEL | FLI Proline |  |  |  |  | 4.816 | 71.529 | 0.8 | 1.211 | 65.449 | 3.2 |  |  |  |  | 2.36 | 1/29/2021 |  | 1/29/2021 |  | PSEL | ./EL/3851_22_3_01292021_80.tiff | ./EL/3851_22_3_01292021_20.tiff | ./IV/3851_22_3_01272021.csv | 0 | 1 | 2 | ./RefIV/3851_22_3_01272021.csv | 8.862 | 9.248 | 2018-11-01 | 17:57 | 1.0011 | 0.99893
161 | 3837 |  | 22 | 3 |  | 16690 |  | mono-Si module |  |  | OE 740 days | 6.03 | 69.6 | 5.65 | 0.93698 | 57.6 | 0.82759 | 325 | 6.012 | 69.37 | 5.694 | 0.94711 | 57.48 | 0.8286 | 327.3 | 78.5 | 25.3 | back of panel |  | SPIRE | 4600SLP | 1/21/2020 | 10:15 | PSEL | FLI Proline |  |  |  |  | 4.811 | 71.792 | 0.8 | 1.201 | 66.637 | 3.2 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3837_22_3_01172020_80.tiff | ./EL/3837_22_3_01172020_20.tiff | ./IV/3837_22_3_01212020.csv | 0 | 0 | 2 | ./RefIV/3837_22_3_01212020.csv | 8.862 | 9.248 | 2018-11-01 | 13:15 | 1.0108 | 1.0012
162 | 3837 |  | 22 | 3 |  | 16690 |  | mono-Si module |  |  | OE 1112 days | 6.03 | 69.6 | 5.65 | 0.93698 | 57.6 | 0.82759 | 325 | 6.017 | 69.12 | 5.64 | 0.93734 | 56.94 | 0.82378 | 321.2 | 77.2 | 25 | back of panel |  | SPIRE | 4600SLP | 1/27/2021 | 16:01 | PSEL | FLI Proline |  |  |  |  | 4.811 | 71.492 | 0.8 | 1.206 | 65.412 | 3.2 |  |  |  |  | 2.36 | 1/29/2021 |  | 1/29/2021 |  | PSEL | ./EL/3837_22_3_01292021_80.tiff | ./EL/3837_22_3_01292021_20.tiff | ./IV/3837_22_3_01272021.csv | 0 | 1 | 2 | ./RefIV/3837_22_3_01272021.csv | 8.862 | 9.248 | 2018-11-01 | 13:15 | 1.0004 | 0.99541
163 | 3849 |  | 22 | 3 |  | 16690 |  | mono-Si module |  |  | OE 740 days | 6.03 | 69.6 | 5.65 | 0.93698 | 57.6 | 0.82759 | 325 | 6.006 | 69.46 | 5.7 | 0.94905 | 57.73 | 0.83113 | 329.1 | 78.9 | 25.4 | back of panel |  | SPIRE | 4600SLP | 1/21/2020 | 10:27 | PSEL | FLI Proline |  |  |  |  | 4.811 | 71.867 | 0.8 | 1.206 | 65.9 | 3.2 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3849_22_3_01172020_80.tiff | ./EL/3849_22_3_01172020_20.tiff | ./IV/3849_22_3_01212020.csv | 0 | 0 | 2 | ./RefIV/3849_22_3_01212020.csv | 8.862 | 9.248 | 2018-11-01 | 17:41 | 1.0129 | 1.0043
164 | 3849 |  | 22 | 3 |  | 16690 |  | mono-Si module |  |  | OE 1112 days | 6.03 | 69.6 | 5.65 | 0.93698 | 57.6 | 0.82759 | 325 | 6.005 | 69.21 | 5.635 | 0.93838 | 57.28 | 0.82763 | 322.8 | 77.7 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/27/2021 | 15:49 | PSEL | FLI Proline |  |  |  |  | 4.811 | 71.599 | 0.8 | 1.201 | 65.524 | 3.2 |  |  |  |  | 2.36 | 1/29/2021 |  | 1/29/2021 |  | PSEL | ./EL/3849_22_3_01292021_80.tiff | ./EL/3849_22_3_01292021_20.tiff | ./IV/3849_22_3_01272021.csv | 0 | 1 | 2 | ./RefIV/3849_22_3_01272021.csv | 8.862 | 9.248 | 2018-11-01 | 17:41 | 1.0015 | 1
165 | 3833 |  | 22 | 3 |  | 16690 |  | mono-Si module |  |  | OE 740 days | 6.03 | 69.6 | 5.65 | 0.93698 | 57.6 | 0.82759 | 325 | 6.021 | 69.39 | 5.703 | 0.94718 | 57.51 | 0.82879 | 328 | 78.5 | 25.3 | back of panel |  | SPIRE | 4600SLP | 1/21/2020 | 10:18 | PSEL | FLI Proline |  |  |  |  | 4.821 | 71.829 | 0.8 | 1.206 | 65.712 | 3.2 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3833_22_3_01172020_80.tiff | ./EL/3833_22_3_01172020_20.tiff | ./IV/3833_22_3_01212020.csv | 0 | 0 | 2 | ./RefIV/3833_22_3_01212020.csv | 8.862 | 9.248 | 2018-11-01 | 11:16 | 1.0109 | 1.0015
166 | 3833 |  | 22 | 3 |  | 16690 |  | mono-Si module |  |  | OE 1112 days | 6.03 | 69.6 | 5.65 | 0.93698 | 57.6 | 0.82759 | 325 | 6.019 | 69.16 | 5.642 | 0.93737 | 57.08 | 0.82533 | 322 | 77.4 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/27/2021 | 15:57 | PSEL | FLI Proline |  |  |  |  | 4.816 | 71.492 | 0.8 | 1.211 | 65.374 | 3.2 |  |  |  |  | 2.36 | 1/29/2021 |  | 1/29/2021 |  | PSEL | ./EL/3833_22_3_01292021_80.tiff | ./EL/3833_22_3_01292021_20.tiff | ./IV/3833_22_3_01272021.csv | 0 | 1 | 2 | ./RefIV/3833_22_3_01272021.csv | 8.862 | 9.248 | 2018-11-01 | 11:16 | 1.0004 | 0.99728
167 | 4086 |  | 22 | 3 |  | 16690 |  | mono-Si module |  |  | OE 552 days | 6.03 | 69.6 | 5.65 | 0.93698 | 57.6 | 0.82759 | 325 | 6.011 | 70.46 | 5.685 | 0.94577 | 58.63 | 0.8321 | 333.3 | 78.7 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/21/2020 | 10:32 | PSEL | FLI Proline |  |  |  |  | 4.816 | 73.181 | 0.8 | 1.201 | 67.101 | 3.2 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/4086_22_3_01172020_80.tiff | ./EL/4086_22_3_01172020_20.tiff | ./IV/4086_22_3_01212020.csv | 0 | 0 | 2 | ./RefIV/4086_22_3_01212020.csv | 8.862 | 8.862 | 7/18/2018 | 15:15 | 1.0094 | 1.0055
168 | 4086 |  | 22 | 3 |  | 16690 |  | mono-Si module |  |  | OE 924 days | 6.03 | 69.6 | 5.65 | 0.93698 | 57.6 | 0.82759 | 325 | 6.027 | 70.41 | 5.61 | 0.93081 | 58.34 | 0.82858 | 327.2 | 77.1 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/27/2021 | 15:20 | PSEL | FLI Proline |  |  |  |  | 4.816 | 72.918 | 0.8 | 1.211 | 66.8 | 3.2 |  |  |  |  | 2.36 | 1/29/2021 |  | 1/29/2021 |  | PSEL | ./EL/4086_22_3_01292021_80.tiff | ./EL/4086_22_3_01292021_20.tiff | ./IV/4086_22_3_01272021.csv | 0 | 1 | 2 | ./RefIV/4086_22_3_01272021.csv | 8.862 | 8.862 | 7/18/2018 | 15:15 | 0.99341 | 1.0012
169 | 3842 |  | 22 | 3 |  | 16690 |  | mono-Si module |  |  | OE 740 days | 6.03 | 69.6 | 5.65 | 0.93698 | 57.6 | 0.82759 | 325 | 6.016 | 69.54 | 5.704 | 0.94814 | 57.7 | 0.82974 | 329.1 | 78.7 | 25.3 | back of panel |  | SPIRE | 4600SLP | 1/21/2020 | 10:21 | PSEL | FLI Proline |  |  |  |  | 4.806 | 71.98 | 0.8 | 1.201 | 66.9 | 3.2 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3842_22_3_01172020_80.tiff | ./EL/3842_22_3_01172020_20.tiff | ./IV/3842_22_3_01212020.csv | 0 | 0 | 2 | ./RefIV/3842_22_3_01212020.csv | 8.862 | 9.248 | 2018-11-01 | 16:40 | 1.0119 | 1.0026
170 | 3842 |  | 22 | 3 |  | 16690 |  | mono-Si module |  |  | OE 1112 days | 6.03 | 69.6 | 5.65 | 0.93698 | 57.6 | 0.82759 | 325 | 6.021 | 69.3 | 5.649 | 0.93822 | 57.22 | 0.82569 | 323.2 | 77.5 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/27/2021 | 15:52 | PSEL | FLI Proline | [7 empty] | 1.211 | 65.599 | 3.2 |  |  |  |  | 2.36 | 1/29/2021 |  | 1/29/2021 |  | PSEL |  | ./EL/3842_22_3_01292021_20.tiff | ./IV/3842_22_3_01272021.csv | 0 | 1 | 2 | ./RefIV/3842_22_3_01272021.csv | 8.862 | 9.248 | 2018-11-01 | 16:40 | 1.0013 | 0.9977
171 | 3832 |  | 22 | 3 |  | 16690 |  | mono-Si module |  |  | OE 740 days | 6.03 | 69.6 | 5.65 | 0.93698 | 57.6 | 0.82759 | 325 | 6.009 | 69.46 | 5.7 | 0.94858 | 57.61 | 0.8294 | 328.4 | 78.7 | 25.2 | back of panel |  | SPIRE | 4600SLP | 1/21/2020 | 10:17 | PSEL | FLI Proline |  |  |  |  | 4.811 | 71.867 | 0.8 | 1.201 | 66.787 | 3.2 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3832_22_3_01172020_80.tiff | ./EL/3832_22_3_01172020_20.tiff | ./IV/3832_22_3_01212020.csv | 0 | 0 | 2 | ./RefIV/3832_22_3_01212020.csv | 8.862 | 9.248 | 2018-11-01 | 11:06 | 1.0124 | 1.0022
172 | 3832 |  | 22 | 3 |  | 16690 |  | mono-Si module |  |  | OE 1112 days | 6.03 | 69.6 | 5.65 | 0.93698 | 57.6 | 0.82759 | 325 | 6.012 | 69.23 | 5.642 | 0.93846 | 57.15 | 0.82551 | 322.4 | 77.5 | 25 | back of panel |  | SPIRE | 4600SLP | 1/27/2021 | 15:56 | PSEL | FLI Proline |  |  |  |  | 4.816 | 71.529 | 0.8 | 1.211 | 65.412 | 3.2 |  |  |  |  | 2.36 | 1/29/2021 |  | 1/29/2021 |  | PSEL | ./EL/3832_22_3_01292021_80.tiff | ./EL/3832_22_3_01292021_20.tiff | ./IV/3832_22_3_01272021.csv | 0 | 1 | 2 | ./RefIV/3832_22_3_01272021.csv | 8.862 | 9.248 | 2018-11-01 | 11:06 | 1.0016 | 0.99749
173 | 3831 |  | 22 | 3 |  | 16690 |  | mono-Si module |  |  | OE 740 days | 6.03 | 69.6 | 5.65 | 0.93698 | 57.6 | 0.82759 | 325 | 6.015 | 69.47 | 5.692 | 0.9463 | 57.6 | 0.82913 | 327.9 | 78.5 | 25.3 | back of panel |  | SPIRE | 4600SLP | 1/21/2020 | 10:20 | PSEL | FLI Proline |  |  |  |  | 4.816 | 71.942 | 0.8 | 1.206 | 65.824 | 3.2 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3831_22_3_01172020_80.tiff | ./EL/3831_22_3_01172020_20.tiff | ./IV/3831_22_3_01212020.csv | 0 | 0 | 2 | ./RefIV/3831_22_3_01212020.csv | 8.862 | 9.248 | 2018-11-01 | 10:57 | 1.0099 | 1.0019
174 | 3831 |  | 22 | 3 |  | 16690 |  | mono-Si module |  |  | OE 1112 days | 6.03 | 69.6 | 5.65 | 0.93698 | 57.6 | 0.82759 | 325 | 6.014 | 69.23 | 5.627 | 0.93565 | 57.18 | 0.82594 | 321.8 | 77.3 | 25 | back of panel |  | SPIRE | 4600SLP | 1/27/2021 | 15:59 | PSEL | FLI Proline |  |  |  |  | 1.206 | 71.567 | 0.8 | 1.206 | 65.524 | 3.2 |  |  |  |  | 2.36 | 1/29/2021 |  | 1/29/2021 |  | PSEL | ./EL/3831_22_3_01292021_80.tiff | ./EL/3831_22_3_01292021_20.tiff | ./IV/3831_22_3_01272021.csv | 0 | 1 | 2 | ./RefIV/3831_22_3_01272021.csv | 8.862 | 9.248 | 2018-11-01 | 10:57 | 0.99858 | 0.99801
175 | 3843 |  | 22 | 3 |  | 16690 |  | mono-Si module |  |  | OE 740 days | 6.03 | 69.6 | 5.65 | 0.93698 | 57.6 | 0.82759 | 325 | 6.001 | 69.55 | 5.696 | 0.94918 | 57.72 | 0.82991 | 328.8 | 78.8 | 25.4 | back of panel |  | SPIRE | 4600SLP | 1/21/2020 | 10:23 | PSEL | FLI Proline |  |  |  |  | 4.811 | 71.98 | 0.8 | 1.201 | 66.682 | 3.2 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3843_22_3_01172020_80.tiff | ./EL/3843_22_3_01172020_20.tiff | ./IV/3843_22_3_01212020.csv | 0 | 0 | 2 | ./RefIV/3843_22_3_01212020.csv | 8.862 | 9.248 | 2018-11-01 | 16:51 | 1.013 | 1.0028
176 | 3843 |  | 22 | 3 |  | 16690 |  | mono-Si module |  |  | OE 1112 days | 6.03 | 69.6 | 5.65 | 0.93698 | 57.6 | 0.82759 | 325 | 6.006 | 69.29 | 5.641 | 0.93923 | 57.2 | 0.82552 | 322.7 | 77.5 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/27/2021 | 15:55 | PSEL | FLI Proline |  |  |  |  | 4.816 | 71.717 | 0.8 | 1.211 | 65.599 | 3.2 |  |  |  |  | 2.36 | 1/29/2021 |  | 1/29/2021 |  | PSEL | ./EL/3843_22_3_01292021_80.tiff | ./EL/3843_22_3_01292021_20.tiff | ./IV/3843_22_3_01272021.csv | 0 | 1 | 2 | ./RefIV/3843_22_3_01272021.csv | 8.862 | 9.248 | 2018-11-01 | 16:51 | 1.0024 | 0.9975
177 | 4082 |  | 22 | 3 |  | 16690 |  | mono-Si module |  |  | OE 552 days | 6.03 | 69.6 | 5.65 | 0.93698 | 57.6 | 0.82759 | 325 | 6.007 | 69.71 | 5.679 | 0.9454 | 57.96 | 0.83144 | 329.2 | 78.6 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/21/2020 | 10:06 | PSEL | FLI Proline |  |  |  |  | 4.886 | 71.905 | 0.8 | 1.206 | 66.102 | 3.2 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/4082_22_3_01172020_80.tiff | ./EL/4082_22_3_01172020_20.tiff | ./IV/4082_22_3_01212020.csv | 0 | 0 | 1 | ./RefIV/4082_22_3_01212020.csv | 8.862 | 8.862 | 7/18/2018 | 14:51 | 1.009 | 1.0047
178 | 4067 |  | 22 | 3 |  | 16690 |  | mono-Si module |  |  | OE 552 days | 6.03 | 69.6 | 5.65 | 0.93698 | 57.6 | 0.82759 | 325 | 5.999 | 69.89 | 5.682 | 0.94716 | 57.97 | 0.82945 | 329.4 | 78.6 | 25.2 | back of panel |  | SPIRE | 4600SLP | 1/21/2020 | 10:12 | PSEL | FLI Proline |  |  |  |  | 4.811 | 72.43 | 0.8 | 1.206 | 66.312 | 3.2 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/4067_22_3_01172020_80.tiff | ./EL/4067_22_3_01172020_20.tiff | ./IV/4067_22_3_01212020.csv | 0 | 0 | 1 | ./RefIV/4067_22_3_01212020.csv | 8.862 | 8.862 | 7/18/2018 | 12:35 | 1.0109 | 1.0022
179 | 4072 |  | 22 | 3 |  | 16690 |  | mono-Si module |  |  | OE 552 days | 6.03 | 69.6 | 5.65 | 0.93698 | 57.6 | 0.82759 | 325 | 6.007 | 70.44 | 5.688 | 0.9469 | 58.63 | 0.83234 | 333.4 | 78.8 | 25 | back of panel |  | SPIRE | 4600SLP | 1/21/2020 | 10:34 | PSEL | FLI Proline |  |  |  |  | 4.811 | 73.181 | 0.8 | 1.201 | 67.138 | 3.1 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/4072_22_3_01172020_80.tiff | ./EL/4072_22_3_01172020_20.tiff | ./IV/4072_22_3_01212020.csv | 0 | 0 | 2 | ./RefIV/4072_22_3_01212020.csv | 8.862 | 8.862 | 7/18/2018 | 13:21 | 1.0106 | 1.0057
180 | 4072 |  | 22 | 3 |  | 16690 |  | mono-Si module |  |  | OE 924 days | 6.03 | 69.6 | 5.65 | 0.93698 | 57.6 | 0.82759 | 325 | 5.999 | 70.28 | 5.606 | 0.93449 | 58.29 | 0.8294 | 326.8 | 77.5 | 25.3 | back of panel |  | SPIRE | 4600SLP | 1/27/2021 | 15:09 | PSEL | FLI Proline |  |  |  |  | 4.816 | 72.805 | 0.8 | 1.206 | 66.763 | 3.2 |  |  |  |  | 2.36 | 1/29/2021 |  | 1/29/2021 |  | PSEL | ./EL/4072_22_3_01292021_80.tiff | ./EL/4072_22_3_01292021_20.tiff | ./IV/4072_22_3_01272021.csv | 0 | 1 | 2 | ./RefIV/4072_22_3_01272021.csv | 8.862 | 8.862 | 7/18/2018 | 13:21 | 0.99734 | 1.0022
181 | 4074 |  | 22 | 3 |  | 16690 |  | mono-Si module |  |  | OE 924 days | 6.03 | 69.6 | 5.65 | 0.93698 | 57.6 | 0.82759 | 325 | 6.005 | 69.61 | 5.625 | 0.93672 | 57.5 | 0.82603 | 323.5 | 77.4 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/27/2021 | 16:03 | PSEL | FLI Proline |  |  |  |  | 4.821 | 72.055 | 0.8 | 1.206 | 66.05 | 3.2 |  |  |  |  | 2.36 | 1/29/2021 |  | 1/29/2021 |  | PSEL | ./EL/4074_22_3_01292021_80.tiff | ./EL/4074_22_3_01292021_20.tiff | ./IV/4074_22_3_01272021.csv | 0 | 0 | 1 | ./RefIV/4074_22_3_01272021.csv | 8.862 | 8.862 | 7/18/2018 | 13:30 | 0.99972 | 0.99812
182 | 4084 |  | 22 | 3 |  | 16690 |  | mono-Si module |  |  | OE 924 days | 6.03 | 69.6 | 5.65 | 0.93698 | 57.6 | 0.82759 | 325 | 6.022 | 69.51 | 5.627 | 0.93441 | 57.46 | 0.82664 | 323.3 | 77.2 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/27/2021 | 16:02 | PSEL | FLI Proline |  |  |  |  | 4.816 | 71.905 | 0.8 | 1.206 | 65.162 | 3.2 |  |  |  |  | 2.36 | 1/29/2021 |  | 1/29/2021 |  | PSEL | ./EL/4084_22_3_01292021_80.tiff | ./EL/4084_22_3_01292021_20.tiff | ./IV/4084_22_3_01272021.csv | 0 | 0 | 1 | ./RefIV/4084_22_3_01272021.csv | 8.862 | 8.862 | 7/18/2018 | 14:59 | 0.99725 | 0.99886
183 | 3921 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 189 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.402 | 39.65 | 8.978 | 0.9549 | 32.42 | 0.81765 | 291.1 | 78.1 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/24/2020 | 10:49 | PSEL | FLI Proline |  |  |  |  | 7.513 | 41.392 | 12.8 | 1.88 | 37.451 | 38.4 |  |  |  |  | 2.36 | 1/23/2020 |  | 1/23/2020 |  | PSEL | ./EL/3921_20_1_01232020_80.tiff | ./EL/3921_20_1_01232020_20.tiff | ./IV/3921_20_1_01242020.csv | 0 | 0 | 2 | ./RefIV/3921_20_1_01242020.csv | 8.862 | 8.862 | 7/19/2019 | 11:49 | 1.0007 | 1.0016
184 | 3921 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 564 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.389 | 39.62 | 8.965 | 0.95484 | 32.31 | 0.8155 | 289.6 | 77.9 | 25 | back of panel |  | SPIRE | 4600SLP | 2021-02-02 | 10:27 | PSEL | FLI Proline |  |  |  |  | 7.498 | 41.016 | 12.8 | 1.88 | 37.113 | 38.4 |  |  |  |  | 2.36 | 2021-04-02 |  | 2021-04-02 |  | PSEL | ./EL/3921_20_1_02042021_80.tiff | ./EL/3921_20_1_02042021_20.tiff | ./IV/3921_20_1_02022021.csv | 0 | 1 | 2 | ./RefIV/3921_20_1_02022021.csv | 8.862 | 8.862 | 7/19/2019 | 11:49 | 1.0007 | 0.99898
185 | 4327 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 227 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.396 | 39.54 | 8.984 | 0.95615 | 32.24 | 0.81538 | 289.7 | 78 | 25 | back of panel |  | SPIRE | 4600SLP | 1/24/2020 | 10:54 | PSEL | FLI Proline |  |  |  |  | 7.508 | 41.316 | 12.8 | 1.875 | 37.388 | 38.4 |  |  |  |  | 2.36 | 1/23/2020 |  | 1/23/2020 |  | PSEL | ./EL/4327_20_1_01232020_80.tiff | ./EL/4327_20_1_01232020_20.tiff | ./IV/4327_20_1_01242020.csv | 0 | 0 | 2 | ./RefIV/4327_20_1_01242020.csv | 8.862 | 8.862 | 2019-11-06 | 15:04 | 1.002 | 0.99884
186 | 4327 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 602 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.379 | 39.52 | 8.973 | 0.95671 | 32.12 | 0.81275 | 288.2 | 77.7 | 24.8 | back of panel |  | SPIRE | 4600SLP | 2021-02-02 | 10:44 | PSEL | FLI Proline |  |  |  |  | 7.498 | 41.091 | 12.8 | 1.88 | 37.075 | 38.4 |  |  |  |  | 2.36 | 2021-04-02 |  | 2021-04-02 |  | PSEL | ./EL/4327_20_1_02042021_80.tiff | ./EL/4327_20_1_02042021_20.tiff | ./IV/4327_20_1_02022021.csv | 0 | 1 | 2 | ./RefIV/4327_20_1_02022021.csv | 8.862 | 8.862 | 2019-11-06 | 15:04 | 1.0026 | 0.99562
187 | 4265 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 402 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.402 | 39.52 | 8.981 | 0.95522 | 32.21 | 0.81503 | 289.3 | 77.9 | 25.2 | back of panel |  | SPIRE | 4600SLP | 1/24/2020 | 11:05 | PSEL | FLI Proline |  |  |  |  | 7.508 | 41.392 | 12.8 | 1.88 | 37.413 | 38.4 |  |  |  |  | 2.36 | 1/23/2020 |  | 1/23/2020 |  | PSEL | ./EL/4265_20_1_01232020_80.tiff | ./EL/4265_20_1_01232020_20.tiff | ./IV/4265_20_1_01242020.csv | 0 | 0 | 2 | ./RefIV/4265_20_1_01242020.csv | 8.862 | 8.862 | 12/18/2018 | 8:36 | 1.0011 | 0.99841
188 | 4265 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 777 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.361 | 39.48 | 8.952 | 0.95631 | 32.03 | 0.8113 | 286.7 | 77.6 | 25.4 | back of panel |  | SPIRE | 4600SLP | 2021-02-02 | 10:36 | PSEL | FLI Proline |  |  |  |  | 7.498 | 41.129 | 12.8 | 1.88 | 37.113 | 38.4 |  |  |  |  | 2.36 | 2021-04-02 |  | 2021-04-02 |  | PSEL | ./EL/4265_20_1_02042021_80.tiff | ./EL/4265_20_1_02042021_20.tiff | ./IV/4265_20_1_02022021.csv | 0 | 1 | 2 | ./RefIV/4265_20_1_02022021.csv | 8.862 | 8.862 | 12/18/2018 | 8:36 | 1.0022 | 0.99384
189 | 4270 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 402 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.387 | 39.52 | 8.974 | 0.956 | 32.14 | 0.81326 | 288.5 | 77.8 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/24/2020 | 10:59 | PSEL | FLI Proline |  |  |  |  | 7.503 | 42.279 | 12.8 | 1.88 | 37.301 | 38.4 |  |  |  |  | 2.36 | 1/23/2020 |  | 1/23/2020 |  | PSEL | ./EL/4270_20_1_01232020_80.tiff | ./EL/4270_20_1_01232020_20.tiff | ./IV/4270_20_1_01242020.csv | 0 | 0 | 2 | ./RefIV/4270_20_1_01242020.csv | 8.862 | 8.862 | 12/18/2018 | 10:02 | 1.0019 | 0.99624
190 | 4270 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 777 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.375 | 39.52 | 8.958 | 0.95552 | 31.94 | 0.8082 | 286.2 | 77.2 | 24.8 | back of panel |  | SPIRE | 4600SLP | 2021-02-02 | 10:46 | PSEL | FLI Proline |  |  |  |  | 7.498 | 41.129 | 12.8 | [7 empty] | 2.36 | 2021-04-02 |  | 2021-04-02 |  | PSEL | ./EL/4270_20_1_02042021_80.tiff |  | ./IV/4270_20_1_02022021.csv | 0 | 1 | 2 | ./RefIV/4270_20_1_02022021.csv | 8.862 | 8.862 | 12/18/2018 | 10:02 | 1.0014 | 0.99004
191 | 4326 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 227 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.375 | 39.47 | 8.944 | 0.95403 | 32.23 | 0.81657 | 288.3 | 77.9 | 25 | back of panel |  | SPIRE | 4600SLP | 1/24/2020 | 10:55 | PSEL | FLI Proline |  |  |  |  | 7.513 | 41.204 | 12.8 | 1.88 | 37.226 | 38.4 |  |  |  |  | 2.36 | 1/23/2020 |  | 1/23/2020 |  | PSEL | ./EL/4326_20_1_01232020_80.tiff | ./EL/4326_20_1_01232020_20.tiff | ./IV/4326_20_1_01242020.csv | 0 | 0 | 2 | ./RefIV/4326_20_1_01242020.csv | 8.862 | 8.862 | 2019-11-06 | 14:59 | 0.9998 | 1.0003
192 | 4326 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 602 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.365 | 39.42 | 8.918 | 0.95227 | 32.02 | 0.81228 | 285.6 | 77.4 | 24.8 | back of panel |  | SPIRE | 4600SLP | 2021-02-02 | 10:43 | PSEL | FLI Proline |  |  |  |  | 7.498 | 41.054 | 12.8 | 1.88 | 36.693 | 38.4 |  |  |  |  | 2.36 | 2021-04-02 |  | 2021-04-02 |  | PSEL | ./EL/4326_20_1_02042021_80.tiff | ./EL/4326_20_1_02042021_20.tiff | ./IV/4326_20_1_02022021.csv | 0 | 1 | 2 | ./RefIV/4326_20_1_02022021.csv | 8.862 | 8.862 | 2019-11-06 | 14:59 | 0.99796 | 0.99504
193 | 4317 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 226 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.401 | 39.54 | 8.968 | 0.95394 | 32.27 | 0.81614 | 289.3 | 77.8 | 25.3 | back of panel |  | SPIRE | 4600SLP | 1/24/2020 | 11:07 | PSEL | FLI Proline |  |  |  |  | 7.508 | 41.392 | 12.8 | 1.88 | 37.451 | 38.4 |  |  |  |  | 2.36 | 1/23/2020 |  | 1/23/2020 |  | PSEL | ./EL/4317_20_1_01232020_80.tiff | ./EL/4317_20_1_01232020_20.tiff | ./IV/4317_20_1_01242020.csv | 0 | 0 | 2 | ./RefIV/4317_20_1_01242020.csv | 8.862 | 8.862 | 2019-12-06 | 11:13 | 0.99971 | 0.99977
194 | 4317 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 601 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.37 | 39.53 | 8.947 | 0.95486 | 32.1 | 0.81204 | 287.2 | 77.5 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-02-02 | 10:39 | PSEL | FLI Proline |  |  |  |  | 7.498 | 41.166 | 12.8 | 1.88 | 37.151 | 38.4 |  |  |  |  | 2.36 | 2021-04-02 |  | 2021-04-02 |  | PSEL | ./EL/4317_20_1_02042021_80.tiff | ./EL/4317_20_1_02042021_20.tiff | ./IV/4317_20_1_02022021.csv | 0 | 1 | 2 | ./RefIV/4317_20_1_02022021.csv | 8.862 | 8.862 | 2019-12-06 | 11:13 | 1.0007 | 0.99475
195 | 4262 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 402 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.396 | 39.6 | 8.981 | 0.95583 | 32.26 | 0.81465 | 289.7 | 77.9 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/24/2020 | 10:51 | PSEL | FLI Proline |  |  |  |  | 7.513 | 41.279 | 12.8 | 1.88 | 37.262 | 38.4 |  |  |  |  | 2.36 | 1/23/2020 |  | 1/23/2020 |  | PSEL | ./EL/4262_20_1_01232020_80.tiff | ./EL/4262_20_1_01232020_20.tiff | ./IV/4262_20_1_01242020.csv | 0 | 0 | 2 | ./RefIV/4262_20_1_01242020.csv | 8.862 | 8.862 | 12/18/2018 | 12:21 | 1.0017 | 0.99794
196 | 4262 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 777 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.382 | 39.51 | 8.955 | 0.95449 | 32.02 | 0.81043 | 286.7 | 77.4 | 25.4 | back of panel |  | SPIRE | 4600SLP | 2021-02-02 | 10:33 | PSEL | FLI Proline |  |  |  |  | 7.498 | 41.241 | 12.8 | 1.88 | 37.188 | 38.4 |  |  |  |  | 2.36 | 2021-04-02 |  | 2021-04-02 |  | PSEL | ./EL/4262_20_1_02042021_80.tiff | ./EL/4262_20_1_02042021_20.tiff | ./IV/4262_20_1_02022021.csv | 0 | 1 | 2 | ./RefIV/4262_20_1_02022021.csv | 8.862 | 8.862 | 12/18/2018 | 12:21 | 1.0003 | 0.99277
197 | 4331 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 227 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.355 | 39.59 | 8.947 | 0.95639 | 32.35 | 0.81713 | 289.4 | 78.2 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/24/2020 | 11:01 | PSEL | FLI Proline |  |  |  |  | 7.508 | 42.392 | 12.8 | 1.88 | 37.451 | 38.4 |  |  |  |  | 2.36 | 1/23/2020 |  | 1/23/2020 |  | PSEL | ./EL/4331_20_1_01232020_80.tiff | ./EL/4331_20_1_01232020_20.tiff | ./IV/4331_20_1_01242020.csv | 0 | 0 | 2 | ./RefIV/4331_20_1_01242020.csv | 8.862 | 8.862 | 2019-11-06 | 15:42 | 1.0023 | 1.001
198 | 4331 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 602 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.351 | 39.57 | 8.924 | 0.95434 | 32.17 | 0.81299 | 287.1 | 77.6 | 25 | back of panel |  | SPIRE | 4600SLP | 2021-02-02 | 10:41 | PSEL | FLI Proline |  |  |  |  | 7.498 | 41.204 | 12.8 | 1.88 | 37.188 | 38.4 |  |  |  |  | 2.36 | 2021-04-02 |  | 2021-04-02 |  | PSEL | ./EL/4331_20_1_02042021_80.tiff | ./EL/4331_20_1_02042021_20.tiff | ./IV/4331_20_1_02022021.csv | 0 | 1 | 2 | ./RefIV/4331_20_1_02022021.csv | 8.862 | 8.862 | 2019-11-06 | 15:42 | 1.0001 | 0.99591
199 | 3922 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 189 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.405 | 39.64 | 8.976 | 0.95439 | 32.43 | 0.81811 | 291.1 | 78.1 | 25 | back of panel |  | SPIRE | 4600SLP | 1/24/2020 | 10:46 | PSEL | FLI Proline |  |  |  |  | 7.508 | 41.354 | 12.8 | 1.88 | 37.451 | 38.4 |  |  |  |  | 2.36 | 1/23/2020 |  | 1/23/2020 |  | PSEL | ./EL/3922_20_1_01232020_80.tiff | ./EL/3922_20_1_01232020_20.tiff | ./IV/3922_20_1_01242020.csv | 0 | 0 | 2 | ./RefIV/3922_20_1_01242020.csv | 8.862 | 8.862 | 7/19/2019 | 11:53 | 1.0002 | 1.0022
200 | 3922 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 564 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.39 | 39.65 | 8.968 | 0.95506 | 32.32 | 0.81513 | 289.9 | 77.9 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-02-02 | 10:29 | PSEL | FLI Proline |  |  |  |  | 7.498 | 41.241 | 12.8 | 1.875 | 37.263 | 38.4 |  |  |  |  | 2.36 | 2021-04-02 |  | 2021-04-02 |  | PSEL | ./EL/3922_20_1_02042021_80.tiff | ./EL/3922_20_1_02042021_20.tiff | ./IV/3922_20_1_02022021.csv | 0 | 1 | 2 | ./RefIV/3922_20_1_02022021.csv | 8.862 | 8.862 | 7/19/2019 | 11:53 | 1.0009 | 0.99854
201 | 4267 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 402 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.394 | 39.62 | 8.988 | 0.95678 | 32.25 | 0.81398 | 289.8 | 77.9 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/24/2020 | 11:00 | PSEL | FLI Proline |  |  |  |  | 7.508 | 41.542 | 12.8 | 1.88 | 37.488 | 38.4 |  |  |  |  | 2.36 | 1/23/2020 |  | 1/23/2020 |  | PSEL | ./EL/4267_20_1_01232020_80.tiff | ./EL/4267_20_1_01232020_20.tiff | ./IV/4267_20_1_01242020.csv | 0 | 0 | 1 | ./RefIV/4267_20_1_01242020.csv | 8.862 | 8.862 | 12/18/2018 | 9:47 | 1.0027 | 0.99713
202 | 4324 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 227 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.385 | 39.59 | 8.98 | 0.95685 | 32.28 | 0.81536 | 289.9 | 78 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/24/2020 | 10:52 | PSEL | FLI Proline |  |  |  |  | 7.513 | 41.392 | 12.8 | 1.88 | 37.376 | 38.4 |  |  |  |  | 2.36 | 1/23/2020 |  | 1/23/2020 |  | PSEL | ./EL/4324_20_1_01232020_80.tiff | ./EL/4324_20_1_01232020_20.tiff | ./IV/4324_20_1_01242020.csv | 0 | 0 | 2 | ./RefIV/4324_20_1_01242020.csv | 8.862 | 8.862 | 2019-11-06 | 14:45 | 1.0028 | 0.99881
203 | 4324 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 602 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.371 | 39.54 | 8.949 | 0.95497 | 32.11 | 0.81209 | 287.4 | 77.5 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2021-02-02 | 10:42 | PSEL | FLI Proline |  |  |  |  | 7.498 | 41.241 | 12.8 | 1.88 | 37.151 | 38.4 |  |  |  |  | 2.36 | 2021-04-02 |  | 2021-04-02 |  | PSEL | ./EL/4324_20_1_02042021_80.tiff | ./EL/4324_20_1_02042021_20.tiff | ./IV/4324_20_1_02022021.csv | 0 | 1 | 2 | ./RefIV/4324_20_1_02022021.csv | 8.862 | 8.862 | 2019-11-06 | 14:45 | 1.0008 | 0.99481
204 | 4318 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 226 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.386 | 39.52 | 8.966 | 0.95525 | 32.15 | 0.81351 | 288.2 | 77.7 | 25.2 | back of panel |  | SPIRE | 4600SLP | 1/24/2020 | 11:06 | PSEL | FLI Proline |  |  |  |  | 7.508 | 41.392 | 12.8 | 1.88 | 37.413 | 38.4 |  |  |  |  | 2.36 | 1/23/2020 |  | 1/23/2020 |  | PSEL | ./EL/4318_20_1_01232020_80.tiff | ./EL/4318_20_1_01232020_20.tiff | ./IV/4318_20_1_01242020.csv | 0 | 0 | 2 | ./RefIV/4318_20_1_01242020.csv | 8.862 | 8.862 | 2019-12-06 | 11:17 | 1.0011 | 0.99655
205 | 4318 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 601 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.362 | 39.49 | 8.935 | 0.95439 | 31.95 | 0.80907 | 285.4 | 77.2 | 25.3 | back of panel |  | SPIRE | 4600SLP | 2021-02-02 | 10:37 | PSEL | FLI Proline |  |  |  |  | 7.498 | 41.241 | 12.8 | 1.88 | 37.151 | 38.4 |  |  |  |  | 2.36 | 2021-04-02 |  | 2021-04-02 |  | PSEL | ./EL/4318_20_1_02042021_80.tiff | ./EL/4318_20_1_02042021_20.tiff | ./IV/4318_20_1_02022021.csv | 0 | 1 | 2 | ./RefIV/4318_20_1_02022021.csv | 8.862 | 8.862 | 2019-12-06 | 11:17 | 1.0002 | 0.99111
206 | 4328 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 227 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.392 | 39.53 | 8.983 | 0.95645 | 32.23 | 0.81533 | 289.5 | 78 | 25 | back of panel |  | SPIRE | 4600SLP | 1/24/2020 | 10:57 | PSEL | FLI Proline |  |  |  |  | 7.508 | 41.354 | 12.8 | 1.88 | 37.336 | 38.4 |  |  |  |  | 2.36 | 1/23/2020 |  | 1/23/2020 |  | PSEL | ./EL/4328_20_1_01232020_80.tiff | ./EL/4328_20_1_01232020_20.tiff | ./IV/4328_20_1_01242020.csv | 0 | 0 | 1 | ./RefIV/4328_20_1_01242020.csv | 8.862 | 8.862 | 2019-11-06 | 15:11 | 1.0023 | 0.99878
207 | 4333 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 227 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.375 | 39.42 | 8.963 | 0.95605 | 32.09 | 0.81405 | 287.6 | 77.8 | 25.2 | back of panel |  | SPIRE | 4600SLP | 1/24/2020 | 11:02 | PSEL | FLI Proline |  |  |  |  | 7.513 | 41.241 | 12.8 | 1.88 | 37.188 | 38.4 |  |  |  |  | 2.36 | 1/23/2020 |  | 1/23/2020 |  | PSEL | ./EL/4333_20_1_01232020_80.tiff | ./EL/4333_20_1_01232020_20.tiff | ./IV/4333_20_1_01242020.csv | 0 | 0 | 2 | ./RefIV/4333_20_1_01242020.csv | 8.862 | 8.862 | 2019-11-06 | 16:05 | 1.0019 | 0.99722
208 | 4333 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 602 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.333 | 39.4 | 8.933 | 0.95714 | 31.97 | 0.81142 | 285.6 | 77.7 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-02-02 | 10:40 | PSEL | FLI Proline |  |  |  |  | 7.498 | 40.979 | 12.8 | 1.88 | 36.963 | 38.4 |  |  |  |  | 2.36 | 2021-04-02 |  | 2021-04-02 |  | PSEL | ./EL/4333_20_1_02042021_80.tiff | ./EL/4333_20_1_02042021_20.tiff | ./IV/4333_20_1_02022021.csv | 0 | 1 | 2 | ./RefIV/4333_20_1_02022021.csv | 8.862 | 8.862 | 2019-11-06 | 16:05 | 1.0031 | 0.99399
209 | 4329 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 227 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.379 | 39.53 | 8.963 | 0.95565 | 32.24 | 0.81558 | 289 | 77.9 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/24/2020 | 10:58 | PSEL | FLI Proline |  |  |  |  | 7.508 | 41.354 | 12.8 | 1.88 | 37.413 | 38.4 |  |  |  |  | 2.36 | 1/23/2020 |  | 1/23/2020 |  | PSEL | ./EL/4329_20_1_01232020_80.tiff | ./EL/4329_20_1_01232020_20.tiff | ./IV/4329_20_1_01242020.csv | 0 | 0 | 1 | ./RefIV/4329_20_1_01242020.csv | 8.862 | 8.862 | 2019-11-06 | 15:23 | 1.0015 | 0.99909
210 | 4336 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 227 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.411 | 39.5 | 8.979 | 0.9541 | 32.21 | 0.81544 | 289.2 | 77.8 | 25.2 | back of panel |  | SPIRE | 4600SLP | 1/24/2020 | 11:04 | PSEL | FLI Proline |  |  |  |  | 7.513 | 41.392 | 12.8 | 1.88 | 37.338 | 38.4 |  |  |  |  | 2.36 | 1/23/2020 |  | 1/23/2020 |  | PSEL | ./EL/4336_20_1_01232020_80.tiff | ./EL/4336_20_1_01232020_20.tiff | ./IV/4336_20_1_01242020.csv | 0 | 0 | 2 | ./RefIV/4336_20_1_01242020.csv | 8.862 | 8.862 | 2019-11-06 | 17:09 | 0.99988 | 0.99892
211 | 4336 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 602 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.388 | 39.47 | 8.955 | 0.95388 | 32.03 | 0.8115 | 286.9 | 77.4 | 25.4 | back of panel |  | SPIRE | 4600SLP | 2021-02-02 | 10:35 | PSEL | FLI Proline |  |  |  |  | 7.498 | 41.166 | 12.8 | 1.88 | 37.113 | 38.4 |  |  |  |  | 2.36 | 2021-04-02 |  | 2021-04-02 |  | PSEL | ./EL/4336_20_1_02042021_80.tiff | ./EL/4336_20_1_02042021_20.tiff | ./IV/4336_20_1_02022021.csv | 0 | 1 | 2 | ./RefIV/4336_20_1_02022021.csv | 8.862 | 8.862 | 2019-11-06 | 17:09 | 0.99965 | 0.99409
212 | 4252 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 779 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.378 | 39.48 | 8.939 | 0.95319 | 31.9 | 0.808 | 285.2 | 77 | 25.4 | back of panel |  | SPIRE | 4600SLP | 2021-04-02 | 10:14 | PSEL | FLI Proline |  |  |  |  | 7.4 | 41.4 | 9.6 | 1.9 | 37.4 | 38.4 |  |  |  |  | 2.36 | 2/16/2021 |  | 2/16/2021 |  | PSEL | ./EL/4252_20_1_02162021_80.tiff | ./EL/4252_20_1_02162021_20.tiff | ./IV/4252_20_1_02042021.csv | 0 | 1 | 2 | ./RefIV/4252_20_1_02042021.csv | 8.862 | 8.862 | 12/18/2018 | 14:17 | 0.99892 | 0.9898
213 | 4252 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 407 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.37 | 39.54 | 8.944 | 0.95454 | 32.19 | 0.81411 | 287.9 | 77.7 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 10:41 | PSEL | FLI Proline |  |  |  |  | 7.503 | 41.579 | 9.6 | 1.88 | 37.488 | 38.4 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4252_20_1_01302020_80.tiff | ./EL/4252_20_1_01302020_20.tiff | ./IV/4252_20_1_01292020.csv | 0 | 0 | 2 | ./RefIV/4252_20_1_01292020.csv | 8.862 | 8.862 | 12/18/2018 | 14:17 | 1.0003 | 0.99729
214 | 4268 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 779 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.368 | 39.47 | 8.945 | 0.95485 | 31.99 | 0.81049 | 286.1 | 77.4 | 25.4 | back of panel |  | SPIRE | 4600SLP | 2021-04-02 | 10:11 | PSEL | FLI Proline |  |  |  |  | 7.4 | 41.5 | 9.6 | 1.9 | 37.3 | 38.4 |  |  |  |  | 2.36 | 2/16/2021 |  | 2/16/2021 |  | PSEL | ./EL/4268_20_1_02162021_80.tiff | ./EL/4268_20_1_02162021_20.tiff | ./IV/4268_20_1_02042021.csv | 0 | 1 | 2 | ./RefIV/4268_20_1_02042021.csv | 8.862 | 8.862 | 12/18/2018 | 12:38 | 1.0007 | 0.99285
215 | 4268 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 407 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.378 | 39.56 | 8.96 | 0.95543 | 32.26 | 0.81547 | 289 | 77.9 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 10:47 | PSEL | FLI Proline |  |  |  |  | 7.508 | 41.542 | 9.6 | 1.88 | 37.488 | 38.4 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4268_20_1_01302020_80.tiff | ./EL/4268_20_1_01302020_20.tiff | ./IV/4268_20_1_01292020.csv | 0 | 0 | 2 | ./RefIV/4268_20_1_01292020.csv | 8.862 | 8.862 | 12/18/2018 | 12:38 | 1.0013 | 0.99895
216 | 4250 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 779 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.374 | 39.52 | 8.952 | 0.95498 | 32.07 | 0.81149 | 287.1 | 77.5 | 25.4 | back of panel |  | SPIRE | 4600SLP | 2021-04-02 | 10:09 | PSEL | FLI Proline |  |  |  |  | 7.4 | 41.3 | 9.6 | 1.9 | 37.7 | 38.4 |  |  |  |  | 2.36 | 2/16/2021 |  | 2/16/2021 |  | PSEL | ./EL/4250_20_1_02162021_80.tiff | ./EL/4250_20_1_02162021_20.tiff | ./IV/4250_20_1_02042021.csv | 0 | 1 | 2 | ./RefIV/4250_20_1_02042021.csv | 8.862 | 8.862 | 12/18/2018 | 13:03 | 1.0008 | 0.99407
217 | 4250 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 407 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.378 | 39.61 | 8.974 | 0.95692 | 32.31 | 0.8157 | 289.9 | 78.1 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 10:37 | PSEL | FLI Proline |  |  |  |  | 7.508 | 41.729 | 9.6 | 1.88 | 37676 | 38.4 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4250_20_1_01302020_80.tiff | ./EL/4250_20_1_01302020_20.tiff | ./IV/4250_20_1_01292020.csv | 0 | 0 | 2 | ./RefIV/4250_20_1_01292020.csv | 8.862 | 8.862 | 12/18/2018 | 13:03 | 1.0028 | 0.99924
218 | 4253 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 779 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.389 | 39.49 | 8.966 | 0.95495 | 31.92 | 0.80831 | 286.2 | 77.2 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-04-02 | 10:21 | PSEL | FLI Proline | [7 empty] | 1.9 | 37.4 | 38.4 |  |  |  |  | 2.36 | 2/16/2021 |  | 2/16/2021 |  | PSEL |  | ./EL/4253_20_1_02162021_20.tiff | ./IV/4253_20_1_02042021.csv | 0 | 1 | 2 | ./RefIV/4253_20_1_02042021.csv | 8.862 | 8.862 | 12/18/2018 | 14:21 | 1.0008 | 0.99017
219 | 4253 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 407 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.375 | 39.51 | 8.964 | 0.95616 | 32.17 | 0.81422 | 288.4 | 77.9 | 25 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 10:45 | PSEL | FLI Proline |  |  |  |  | 7.513 | 41.579 | 9.6 | 1.88 | 37.526 | 38.4 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4253_20_1_01302020_80.tiff | ./EL/4253_20_1_01302020_20.tiff | ./IV/4253_20_1_01292020.csv | 0 | 0 | 2 | ./RefIV/4253_20_1_01292020.csv | 8.862 | 8.862 | 12/18/2018 | 14:21 | 1.002 | 0.99742
220 | 4276 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 779 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.369 | 39.58 | 8.965 | 0.95688 | 32.05 | 0.80975 | 287.4 | 77.5 | 25.4 | back of panel |  | SPIRE | 4600SLP | 2021-04-02 | 10:13 | PSEL | FLI Proline |  |  |  |  | 7.4 | 41.3 | 9.6 | 1.9 | 37.5 | 38.4 |  |  |  |  | 2.36 | 2/16/2021 |  | 2/16/2021 |  | PSEL | ./EL/4276_20_1_02162021_80.tiff | ./EL/4276_20_1_02162021_20.tiff | ./IV/4276_20_1_02042021.csv | 0 | 1 | 2 | ./RefIV/4276_20_1_02042021.csv | 8.862 | 8.862 | 12/18/2018 | 12:45 | 1.0028 | 0.99195
221 | 4276 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 407 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.362 | 39.62 | 8.969 | 0.95802 | 32.31 | 0.8155 | 289.8 | 78.1 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 10:46 | PSEL | FLI Proline |  |  |  |  | 7.503 | 41.617 | 9.6 | 1.88 | 37.601 | 38.4 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4276_20_1_01302020_80.tiff | ./EL/4276_20_1_01302020_20.tiff | ./IV/4276_20_1_01292020.csv | 0 | 0 | 2 | ./RefIV/4276_20_1_01292020.csv | 8.862 | 8.862 | 12/18/2018 | 12:45 | 1.004 | 0.99898
222 | 4251 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 779 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.36 | 39.51 | 8.944 | 0.95556 | 31.93 | 0.80815 | 285.6 | 77.2 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-04-02 | 10:07 | PSEL | FLI Proline |  |  |  |  | 7.4 | 41.2 | 9.6 | 1.9 | 37.4 | 38.4 |  |  |  |  | 2.36 | 2/16/2021 |  | 2/16/2021 |  | PSEL | ./EL/4251_20_1_02162021_80.tiff | ./EL/4251_20_1_02162021_20.tiff | ./IV/4251_20_1_02042021.csv | 0 | 1 | 2 | ./RefIV/4251_20_1_02042021.csv | 8.862 | 8.862 | 12/18/2018 | 14:15 | 1.0014 | 0.98998
223 | 4251 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 407 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.366 | 39.58 | 8.967 | 0.9574 | 32.28 | 0.81556 | 289.4 | 78.1 | 25 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 10:40 | PSEL | FLI Proline |  |  |  |  | 7.513 | 41.579 | 9.6 | 1.88 | 37.526 | 38.4 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4251_20_1_01302020_80.tiff | ./EL/4251_20_1_01302020_20.tiff | ./IV/4251_20_1_01292020.csv | 0 | 0 | 2 | ./RefIV/4251_20_1_01292020.csv | 8.862 | 8.862 | 12/18/2018 | 14:15 | 1.0033 | 0.99907
224 | 4255 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 779 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.37 | 39.55 | 8.967 | 0.95699 | 32.08 | 0.81113 | 287.7 | 77.6 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-04-02 | 10:08 | PSEL | FLI Proline |  |  |  |  | 7.4 | 41.4 | 9.6 | 1.9 | 37.4 | 38.4 |  |  |  |  | 2.36 | 2/16/2021 |  | 2/16/2021 |  | PSEL | ./EL/4255_20_1_02162021_80.tiff | ./EL/4255_20_1_02162021_20.tiff | ./IV/4255_20_1_02042021.csv | 0 | 1 | 2 | ./RefIV/4255_20_1_02042021.csv | 8.862 | 8.862 | 12/18/2018 | 14:24 | 1.0029 | 0.99363
225 | 4255 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 407 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.369 | 39.6 | 8.98 | 0.95848 | 32.31 | 0.81591 | 290.2 | 78.2 | 25 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 10:43 | PSEL | FLI Proline |  |  |  |  | 7.508 | 41.579 | 9.6 | 1.88 | 37.563 | 38.4 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4255_20_1_01302020_80.tiff | ./EL/4255_20_1_01302020_20.tiff | ./IV/4255_20_1_01292020.csv | 0 | 0 | 2 | ./RefIV/4255_20_1_01292020.csv | 8.862 | 8.862 | 12/18/2018 | 14:24 | 1.0045 | 0.99949
226 | 4274 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 779 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.361 | 39.59 | 8.962 | 0.95738 | 32.14 | 0.81182 | 288 | 77.7 | 25.4 | back of panel |  | SPIRE | 4600SLP | 2021-04-02 | 10:10 | PSEL | FLI Proline |  |  |  |  | 7.4 | 41.2 | 9.6 | 1.9 | 41.2 | 38.4 |  |  |  |  | 2.36 | 2/16/2021 |  | 2/16/2021 |  | PSEL | ./EL/4274_20_1_02162021_80.tiff | ./EL/4274_20_1_02162021_20.tiff | ./IV/4274_20_1_02042021.csv | 0 | 1 | 2 | ./RefIV/4274_20_1_02042021.csv | 8.862 | 8.862 | 12/18/2018 | 12:58 | 1.0033 | 0.99448
227 | 4274 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 407 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.386 | 39.66 | 8.971 | 0.95579 | 32.4 | 0.81694 | 290.7 | 78.1 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 10:39 | PSEL | FLI Proline |  |  |  |  | 7.508 | 41.617 | 9.6 | 1.88 | 37.676 | 38.4 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4274_20_1_01302020_80.tiff | ./EL/4274_20_1_01302020_20.tiff | ./IV/4274_20_1_01292020.csv | 0 | 0 | 2 | ./RefIV/4274_20_1_01292020.csv | 8.862 | 8.862 | 12/18/2018 | 12:58 | 1.0016 | 1.0008
228 | 4272 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 779 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.385 | 39.24 | 8.938 | 0.95237 | 31.8 | 0.8104 | 284.3 | 77.2 | 25.3 | back of panel |  | SPIRE | 4600SLP | 2021-04-02 | 10:12 | PSEL | FLI Proline |  |  |  |  | 7.4 | 40.9 | 9.6 | 1.9 | 37 | 38.4 |  |  |  |  | 2.36 | 2/16/2021 |  | 2/16/2021 |  | PSEL | ./EL/4272_20_1_02162021_80.tiff | ./EL/4272_20_1_02162021_20.tiff | ./IV/4272_20_1_02042021.csv | 0 | 1 | 2 | ./RefIV/4272_20_1_02042021.csv | 8.862 | 8.862 | 12/18/2018 | 12:51 | 0.99807 | 0.99274
229 | 4272 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 407 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.386 | 39.31 | 8.945 | 0.95302 | 31.99 | 0.81379 | 286.2 | 77.6 | 25 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 10:36 | PSEL | FLI Proline |  |  |  |  | 7.508 | 41.354 | 9.6 | 1.875 | 37.226 | 38.4 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4272_20_1_01302020_80.tiff | ./EL/4272_20_1_01302020_20.tiff | ./IV/4272_20_1_01292020.csv | 0 | 0 | 2 | ./RefIV/4272_20_1_01292020.csv | 8.862 | 8.862 | 12/18/2018 | 12:51 | 0.99874 | 0.99689
230 | 4273 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 407 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.374 | 39.62 | 8.966 | 0.95648 | 32.31 | 0.8155 | 289.7 | 78 | 25 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 10:49 | PSEL | FLI Proline |  |  |  |  | 7.508 | 41.504 | 9.6 | 1.88 | 37.413 | 38.4 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4273_20_1_01302020_80.tiff | ./EL/4273_20_1_01302020_20.tiff | ./IV/4273_20_1_01292020.csv | 0 | 0 | 1 | ./RefIV/4273_20_1_01292020.csv | 8.862 | 8.862 | 12/18/2018 | 12:54 | 1.0024 | 0.99898
231 | 4261 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 777 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.387 | 39.6 | 8.979 | 0.95654 | 32.11 | 0.81086 | 288.4 | 77.6 | 24.8 | back of panel |  | SPIRE | 4600SLP | 2021-02-02 | 10:45 | PSEL | FLI Proline |  |  |  |  | 7.498 | 41.241 | 12.8 | 1.88 | 37.075 | 38.4 |  |  |  |  | 2.36 | 2021-04-02 |  | 2021-04-02 |  | PSEL | ./EL/4261_20_1_02042021_80.tiff | ./EL/4261_20_1_02042021_20.tiff | ./IV/4261_20_1_02022021.csv | 0 | 0 | 1 | ./RefIV/4261_20_1_02022021.csv | 8.862 | 8.862 | 12/18/2018 | 12:24 | 1.0024 | 0.9933
232 | 4240 |  | 20 | 1 |  | 16626.6 |  | mono-Si module |  |  | OE 778 days | 9.61 | 40.18 | 9.17 | 0.95421 | 32.8 | 0.81633 | 300 | 9.3 | 39.04 | 8.859 | 0.95258 | 31.54 | 0.80789 | 279.4 | 77 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-02-02 | 10:38 | PSEL | FLI Proline |  |  |  |  | 7.498 | 41.641 | 12.8 | 1.88 | 36.437 | 38.4 |  |  |  |  | 2.36 | 2021-04-02 |  | 2021-04-02 |  | PSEL | ./EL/4240_20_1_02042021_80.tiff | ./EL/4240_20_1_02042021_20.tiff | ./IV/4240_20_1_02022021.csv | 0 | 0 | 1 | ./RefIV/4240_20_1_02022021.csv | 8.862 | 8.862 | 12/17/2018 | 14:27 | 0.99829 | 0.98966
233 | 4145 |  | 25 | 1 |  | 16683.3 |  | mono-Si module |  |  | OE 517 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.62 | 39.44 | 9.175 | 0.95374 | 32 | 0.81136 | 293.6 | 77.4 | 25 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 10:59 | PSEL | FLI Proline |  |  |  |  | 7.713 | 41.941 | 9.6 | 1.93 | 37.413 | 51.2 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4145_25_1_01302020_80.tiff | ./EL/4145_25_1_01302020_20.tiff | ./IV/4145_25_1_01292020.csv | 0 | 0 | 1 | ./RefIV/4145_25_1_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 11:35 | 1.0063 | 0.99536
234 | 4137 |  | 25 | 1 |  | 16683.3 |  | mono-Si module |  |  | OE 517 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.637 | 39.55 | 9.19 | 0.95362 | 32.08 | 0.81113 | 294.8 | 77.3 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 11:10 | PSEL | FLI Proline |  |  |  |  | 7.718 | 41.016 | 9.6 | 1.925 | 36.963 | 51.2 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4137_25_1_01302020_80.tiff | ./EL/4137_25_1_01302020_20.tiff | ./IV/4137_25_1_01292020.csv | 0 | 0 | 1 | ./RefIV/4137_25_1_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 10:31 | 1.0061 | 0.99507
235 | 4142 |  | 25 | 1 |  | 16683.3 |  | mono-Si module |  |  | OE 517 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.627 | 39.61 | 9.21 | 0.95668 | 32.21 | 0.81318 | 296.6 | 77.8 | 25 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 11:04 | PSEL | FLI Proline |  |  |  |  | 7.718 | 41.579 | 9.6 | 1.93 | 37.488 | 51.2 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4142_25_1_01302020_80.tiff | ./EL/4142_25_1_01302020_20.tiff | ./IV/4142_25_1_01292020.csv | 0 | 0 | 1 | ./RefIV/4142_25_1_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 11:16 | 1.0094 | 0.99759
236 | 4143 |  | 25 | 1 |  | 16683.3 |  | mono-Si module |  |  | OE 517 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.615 | 39.56 | 9.191 | 0.9559 | 32.18 | 0.81345 | 295.8 | 77.8 | 25 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 11:02 | PSEL | FLI Proline |  |  |  |  | 7.713 | 41.241 | 9.6 | 1.93 | 37.563 | 51.2 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4143_25_1_01302020_80.tiff | ./EL/4143_25_1_01302020_20.tiff | ./IV/4143_25_1_01292020.csv | 0 | 0 | 1 | ./RefIV/4143_25_1_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 11:27 | 1.0085 | 0.99792
237 | 4141 |  | 25 | 1 |  | 16683.3 |  | mono-Si module |  |  | OE 517 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.62 | 39.52 | 9.197 | 0.95603 | 32.1 | 0.81225 | 295.2 | 77.6 | 25 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 11:06 | PSEL | FLI Proline |  |  |  |  | 7.718 | 41.452 | 9.6 | 1.93 | 37.413 | 51.2 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4141_25_1_01302020_80.tiff | ./EL/4141_25_1_01302020_20.tiff | ./IV/4141_25_1_01292020.csv | 0 | 0 | 1 | ./RefIV/4141_25_1_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 11:09 | 1.0087 | 0.99645
238 | 4138 |  | 25 | 1 |  | 16683.3 |  | mono-Si module |  |  | OE 517 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.65 | 39.52 | 9.197 | 0.95306 | 32.09 | 0.81199 | 295.2 | 77.4 | 25 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 11:09 | PSEL | FLI Proline |  |  |  |  | 7.713 | 41.091 | 9.6 | 1.93 | 37 | 51.2 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4138_25_1_01302020_80.tiff | ./EL/4138_25_1_01302020_20.tiff | ./IV/4138_25_1_01292020.csv | 0 | 0 | 1 | ./RefIV/4138_25_1_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 10:48 | 1.0055 | 0.99614
239 | 4146 |  | 25 | 1 |  | 16683.3 |  | mono-Si module |  |  | OE 517 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.636 | 39.55 | 9.18 | 0.95268 | 32.14 | 0.81264 | 295.1 | 77.4 | 25 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 11:00 | PSEL | FLI Proline |  |  |  |  | 7.713 | 40.866 | 9.6 | 1.925 | 37.526 | 51.2 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4146_25_1_01302020_80.tiff | ./EL/4146_25_1_01302020_20.tiff | ./IV/4146_25_1_01292020.csv | 0 | 0 | 1 | ./RefIV/4146_25_1_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 11:40 | 1.0051 | 0.99693
240 | 4140 |  | 25 | 1 |  | 16683.3 |  | mono-Si module |  |  | OE 517 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.638 | 39.53 | 9.197 | 0.95424 | 32.15 | 0.81331 | 295.7 | 77.6 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 11:05 | PSEL | FLI Proline |  |  |  |  | 7.718 | 41.504 | 9.6 | 1.925 | 37.413 | 51.2 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4140_25_1_01302020_80.tiff | ./EL/4140_25_1_01302020_20.tiff | ./IV/4140_25_1_01292020.csv | 0 | 0 | 1 | ./RefIV/4140_25_1_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 10:55 | 1.0068 | 0.99775
241 | 4139 |  | 25 | 1 |  | 16683.3 |  | mono-Si module |  |  | OE 517 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.632 | 39.58 | 9.2 | 0.95515 | 32.21 | 0.81379 | 296.3 | 77.7 | 25 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 11:07 | PSEL | FLI Proline |  |  |  |  | 7.718 | 41.579 | 9.6 | 1.93 | 37.451 | 51.2 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4139_25_1_01302020_80.tiff | ./EL/4139_25_1_01302020_20.tiff | ./IV/4139_25_1_01292020.csv | 0 | 0 | 1 | ./RefIV/4139_25_1_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 10:52 | 1.0078 | 0.99835
242 | 4144 |  | 25 | 1 |  | 16683.3 |  | mono-Si module |  |  | OE 517 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.639 | 39.57 | 9.181 | 0.95248 | 32.11 | 0.81147 | 294.8 | 77.3 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 11:01 | PSEL | FLI Proline |  |  |  |  | 7.718 | 41.729 | 9.6 | 1.93 | 37.563 | 51.2 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4144_25_1_01302020_80.tiff | ./EL/4144_25_1_01302020_20.tiff | ./IV/4144_25_1_01292020.csv | 0 | 0 | 1 | ./RefIV/4144_25_1_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 11:31 | 1.0049 | 0.9955
243 | 3253 |  | 25 | 4 |  | 16700 |  | multi-Si module |  |  | OE 5 days | 9.41 | 38.97 | 8.84 | 0.93943 | 31.67 | 0.81268 | 280 | 9.658 | 38.78 | 9.178 | 0.9503 | 31.07 | 0.80119 | 285.2 | 76.1 | 25.8 | back of panel |  | SPIRE | 4600SLP | 7/24/2017 | 8:40 | PSEL | FLI Proline |  |  |  |  | 7.543 | 40.378 | 19.2 | 1.885 | 36.025 | 72 |  |  |  |  | 2.36 | 2017-01-08 |  | 2017-01-08 |  | PSEL | ./EL/3253_25_4_08012017_80.tiff | ./EL/3253_25_4_08012017_20.tiff | ./IV/3253_25_4_07242017.csv | 0 | 2 | 3 | ./RefIV/3253_25_4_07242017.csv | 9.0256 | 9.0256 | 7/19/2017 | 9:45 | 1.0116 | 0.98586
244 | 3253 |  | 25 | 4 |  | 16700 |  | multi-Si module |  |  | OE 1296 days | 9.41 | 38.97 | 8.84 | 0.93943 | 31.67 | 0.81268 | 280 | 9.513 | 38.89 | 9.039 | 0.95017 | 31.07 | 0.79892 | 280.8 | 75.9 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-04-02 | 13:04 | PSEL | FLI Proline |  |  |  |  | 7.578 | 40.566 | 25.6 | 1.895 | 36.117 | 102.6 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/3253_25_4_02082021_80.tiff | ./EL/3253_25_4_02082021_20.tiff | ./IV/3253_25_4_02042021.csv | 0 | 1 | 3 | ./RefIV/3253_25_4_02042021.csv | 8.862 | 9.0256 | 7/19/2017 | 9:45 | 1.0114 | 0.98307
245 | 3253 |  | 25 | 4 |  | 16700 |  | multi-Si module |  |  | OE 911 days | 9.41 | 38.97 | 8.84 | 0.93943 | 31.67 | 0.81268 | 280 | 9.5 | 38.98 | 9.032 | 0.95074 | 31.29 | 0.80272 | 282.6 | 76.3 | 24.6 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 12:51 | PSEL | FLI Proline |  |  |  |  | 7.573 | 40.416 | 25.6 | 1.895 | 36.262 | 102.6 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/3253_25_4_01202020_80.tiff | ./EL/3253_25_4_01202020_20.tiff | ./IV/3253_25_4_01162020.csv | 0 | 0 | 3 | ./RefIV/3253_25_4_01162020.csv | 8.862 | 9.0256 | 7/19/2017 | 9:45 | 1.012 | 0.98775
246 | 3248 |  | 25 | 3 |  | 16683.3 |  | mono-Si module |  |  | OE 5 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.828 | 39.73 | 9.389 | 0.95533 | 32.26 | 0.81198 | 302.9 | 77.6 | 25 | back of panel |  | SPIRE | 4600SLP | 7/24/2017 | 8:25 | PSEL | FLI Proline |  |  |  |  | 7.828 | 41.016 | 9.6 | 1.96 | 36.963 | 25.6 |  |  |  |  | 2.36 | 2017-01-08 |  | 2017-01-08 |  | PSEL | ./EL/3248_25_3_08012017_80.tiff | ./EL/3248_25_3_08012017_20.tiff | ./IV/3248_25_3_07242017.csv | 0 | 2 | 3 | ./RefIV/3248_25_3_07242017.csv | 9.0256 | 9.0256 | 7/19/2017 | 9:11 | 1.0079 | 0.99612
247 | 3248 |  | 25 | 3 |  | 16683.3 |  | mono-Si module |  |  | OE 1301 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.673 | 39.7 | 9.22 | 0.95317 | 32.09 | 0.80831 | 295.9 | 77 | 25 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 9:36 | PSEL | FLI Proline |  |  |  |  | 7.578 | 41.129 | 12.8 | 1.895 | 36.888 | 51.2 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/3248_25_3_02082021_80.tiff | ./EL/3248_25_3_02082021_20.tiff | ./IV/3248_25_3_02092021.csv | 0 | 1 | 3 | ./RefIV/3248_25_3_02092021.csv | 8.862 | 9.0256 | 7/19/2017 | 9:11 | 1.0057 | 0.99162
248 | 3248 |  | 25 | 3 |  | 16683.3 |  | mono-Si module |  |  | OE 911 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.664 | 39.69 | 9.215 | 0.95354 | 32.22 | 0.81179 | 296.9 | 77.4 | 24.8 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 13:48 | PSEL | FLI Proline |  |  |  |  | 7.693 | 41.241 | 12.8 | 1.92 | 37413 | 51.2 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/3248_25_3_01202020_80.tiff | ./EL/3248_25_3_01202020_20.tiff | ./IV/3248_25_3_01162020.csv | 0 | 0 | 3 | ./RefIV/3248_25_3_01162020.csv | 8.862 | 9.0256 | 7/19/2017 | 9:11 | 1.0061 | 0.99589
249 | 3254 |  | 25 | 4 |  | 16700 |  | multi-Si module |  |  | OE 5 days | 9.41 | 38.97 | 8.84 | 0.93943 | 31.67 | 0.81268 | 280 | 9.624 | 38.82 | 9.143 | 0.95002 | 31.03 | 0.79933 | 283.7 | 75.9 | 25.6 | back of panel |  | SPIRE | 4600SLP | 7/24/2017 | 8:43 | PSEL | FLI Proline |  |  |  |  | 7.543 | 40.378 | 19.2 | 1.885 | 35.987 | 76.8 |  |  |  |  | 2.36 | 2017-01-08 |  | 2017-01-08 |  | PSEL | ./EL/3254_25_4_08012017_80.tiff | ./EL/3254_25_4_08012017_20.tiff | ./IV/3254_25_4_07242017.csv | 0 | 2 | 3 | ./RefIV/3254_25_4_07242017.csv | 9.0256 | 9.0256 | 7/19/2017 | 9:49 | 1.0113 | 0.98358
250 | 3254 |  | 25 | 4 |  | 16700 |  | multi-Si module |  |  | OE 1296 days | 9.41 | 38.97 | 8.84 | 0.93943 | 31.67 | 0.81268 | 280 | 9.477 | 38.88 | 8.999 | 0.94956 | 31 | 0.79733 | 279 | 75.7 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-04-02 | 13:02 | PSEL | FLI Proline |  |  |  |  | 7.578 | 40.603 | 25.6 | 1.895 | 36.1 | 102.6 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/3254_25_4_02082021_80.tiff | ./EL/3254_25_4_02082021_20.tiff | ./IV/3254_25_4_02042021.csv | 0 | 1 | 3 | ./RefIV/3254_25_4_02042021.csv | 8.862 | 9.0256 | 7/19/2017 | 9:49 | 1.0108 | 0.98111
251 | 3254 |  | 25 | 4 |  | 16700 |  | multi-Si module |  |  | OE 911 days | 9.41 | 38.97 | 8.84 | 0.93943 | 31.67 | 0.81268 | 280 | 9.464 | 38.96 | 8.997 | 0.95066 | 31.21 | 0.80108 | 280.8 | 76.1 | 24.6 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 12:56 | PSEL | FLI Proline |  |  |  |  | 7.573 | 40.603 | 25.6 | 1.9 | 36.137 | 102.6 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/3254_25_4_01202020_80.tiff | ./EL/3254_25_4_01202020_20.tiff | ./IV/3254_25_4_01162020.csv | 0 | 0 | 3 | ./RefIV/3254_25_4_01162020.csv | 8.862 | 9.0256 | 7/19/2017 | 9:49 | 1.012 | 0.98573
252 | 3249 |  | 25 | 3 |  | 16683.3 |  | mono-Si module |  |  | OE 5 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.83 | 39.73 | 9.393 | 0.95554 | 32.37 | 0.81475 | 304.1 | 77.9 | 25 | back of panel |  | SPIRE | 4600SLP | 7/24/2017 | 8:28 | PSEL | FLI Proline |  |  |  |  | 7.823 | 41.316 | 9.6 | 1.96 | 37.226 | 25.6 |  |  |  |  | 2.36 | 2017-01-08 |  | 2017-01-08 |  | PSEL | ./EL/3249_25_3_08012017_80.tiff | ./EL/3249_25_3_08012017_20.tiff | ./IV/3249_25_3_07242017.csv | 0 | 2 | 3 | ./RefIV/3249_25_3_07242017.csv | 9.0256 | 9.0256 | 7/19/2017 | 9:24 | 1.0082 | 0.99952
253 | 3249 |  | 25 | 3 |  | 16683.3 |  | mono-Si module |  |  | OE 1301 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.634 | 39.68 | 9.214 | 0.9564 | 32.1 | 0.80897 | 295.8 | 77.4 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 9:34 | PSEL | FLI Proline |  |  |  |  | 7.578 | 46.054 | 12.8 | 1.895 | 36.923 | 51.2 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/3249_25_3_02082021_80.tiff | ./EL/3249_25_3_02082021_20.tiff | ./IV/3249_25_3_02092021.csv | 0 | 1 | 3 | ./RefIV/3249_25_3_02092021.csv | 8.862 | 9.0256 | 7/19/2017 | 9:24 | 1.0091 | 0.99243
254 | 3249 |  | 25 | 3 |  | 16683.3 |  | mono-Si module |  |  | OE 911 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.632 | 39.71 | 9.215 | 0.95671 | 32.3 | 0.8134 | 297.7 | 77.8 | 24.7 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 13:49 | PSEL | FLI Proline |  |  |  |  | 7.693 | 41.429 | 12.8 | 1.925 | 37.451 | 51.2 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/3249_25_3_01202020_80.tiff | ./EL/3249_25_3_01202020_20.tiff | ./IV/3249_25_3_01162020.csv | 0 | 0 | 3 | ./RefIV/3249_25_3_01162020.csv | 8.862 | 9.0256 | 7/19/2017 | 9:24 | 1.0094 | 0.99786
255 | 3246 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 13 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.39 | 37.96 | 8.917 | 0.94963 | 30.91 | 0.81428 | 275.6 | 77.3 | 25.9 | back of panel |  | SPIRE | 4600SLP | 2017-01-08 | 8:35 | PSEL | FLI Proline |  |  |  |  | 7.463 | 39.215 | 38.4 | 1.865 | 35.274 | 102.6 |  |  |  |  | 2.36 | 2017-01-08 |  | 2017-01-08 |  | PSEL | ./EL/3246_5_5_08012017_80.tiff | ./EL/3246_5_5_08012017_20.tiff | ./IV/3246_5_5_08012017.csv | 0 | 2 | 3 | ./RefIV/3246_5_5_08012017.csv | 9.0256 | 9.0256 | 7/19/2017 | 8:58 | 1.0115 | 1.002
256 | 3246 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 1293 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.228 | 38.15 | 8.748 | 0.94798 | 30.87 | 0.80917 | 270.1 | 76.7 | 24.8 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 15:07 | PSEL | FLI Proline |  |  |  |  | 7.338 | 39.252 | 38.4 | 1.84 | 35.274 | 153.6 |  |  |  |  | 2.36 | 2021-02-02 |  | 2021-02-02 |  | PSEL | ./EL/3246_5_5_02022021_80.tiff | ./EL/3246_5_5_02022021_20.tiff | ./IV/3246_5_5_02012021.csv | 0 | 1 | 3 | ./RefIV/3246_5_5_02012021.csv | 8.862 | 9.0256 | 7/19/2017 | 8:58 | 1.0097 | 0.9957
257 | 3246 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 911 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.223 | 38.17 | 8.755 | 0.94926 | 31.16 | 0.81635 | 272.8 | 77.5 | 24.8 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 9:51 | PSEL | FLI Proline |  |  |  |  | 7.363 | 38.764 | 38.4 | 1.84 | 35.349 | 153.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3246_5_5_01172020_80.tiff | ./EL/3246_5_5_01172020_20.tiff | ./IV/3246_5_5_01162020.csv | 0 | 0 | 3 | ./RefIV/3246_5_5_01162020.csv | 8.862 | 9.0256 | 7/19/2017 | 8:58 | 1.0111 | 1.0045
258 | 3245 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 13 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.404 | 37.96 | 8.928 | 0.94938 | 30.92 | 0.81454 | 276.1 | 77.3 | 25.7 | back of panel |  | SPIRE | 4600SLP | 2017-01-08 | 8:37 | PSEL | FLI Proline |  |  |  |  | 7.463 | 38.652 | 38.4 | 1.765 | 34.636 | 102.6 |  |  |  |  | 2.36 | 2017-01-08 |  | 2017-01-08 |  | PSEL | ./EL/3245_5_5_08012017_80.tiff | ./EL/3245_5_5_08012017_20.tiff | ./IV/3245_5_5_08012017.csv | 0 | 2 | 3 | ./RefIV/3245_5_5_08012017.csv | 9.0256 | 9.0256 | 7/19/2017 | 8:46 | 1.0112 | 1.0023
259 | 3245 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 1293 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.235 | 38.12 | 8.758 | 0.94835 | 30.91 | 0.81086 | 270.7 | 76.9 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 15:11 | PSEL | FLI Proline |  |  |  |  | 7.338 | 39.14 | 38.4 | 1.84 | 35.161 | 153.6 |  |  |  |  | 2.36 | 2021-02-02 |  | 2021-02-02 |  | PSEL | ./EL/3245_5_5_02022021_80.tiff | ./EL/3245_5_5_02022021_20.tiff | ./IV/3245_5_5_02012021.csv | 0 | 1 | 3 | ./RefIV/3245_5_5_02012021.csv | 8.862 | 9.0256 | 7/19/2017 | 8:46 | 1.0101 | 0.99778
260 | 3245 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 911 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.231 | 38.18 | 8.765 | 0.94952 | 31.18 | 0.81666 | 273.3 | 77.5 | 24.6 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 9:54 | PSEL | FLI Proline |  |  |  |  | 7.378 | 39.44 | 38.4 | 1.845 | 35.574 | 153.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3245_5_5_01172020_80.tiff | ./EL/3245_5_5_01172020_20.tiff | ./IV/3245_5_5_01162020.csv | 0 | 0 | 3 | ./RefIV/3245_5_5_01162020.csv | 8.862 | 9.0256 | 7/19/2017 | 8:46 | 1.0114 | 1.0049
261 | 3810 |  | 25 | 4 |  | 16700 |  | multi-Si module |  |  | OE 1263 days | 9.41 | 38.97 | 8.84 | 0.93943 | 31.67 | 0.81268 | 280 | 9.446 | 38.59 | 8.961 | 0.94866 | 30.67 | 0.79477 | 274.8 | 75.4 | 25 | back of panel |  | SPIRE | 4600SLP | 2021-04-02 | 13:13 | PSEL | FLI Proline |  |  |  |  | 7.578 | 39.65 | 25.6 | 1.895 | 35.574 | 102.6 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/3810_25_4_02082021_80.tiff | ./EL/3810_25_4_02082021_20.tiff | ./IV/3810_25_4_02042021.csv | 0 | 1 | 2 | ./RefIV/3810_25_4_02042021.csv | 8.862 | 9.0256 | 8/21/2017 | 10:24 | 1.0098 | 0.97796
262 | 3810 |  | 25 | 4 |  | 16700 |  | multi-Si module |  |  | OE 878 days | 9.41 | 38.97 | 8.84 | 0.93943 | 31.67 | 0.81268 | 280 | 9.431 | 38.65 | 8.963 | 0.95038 | 30.88 | 0.79897 | 276.8 | 75.9 | 25 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 13:20 | PSEL | FLI Proline |  |  |  |  | 7.573 | 39.74 | 25.6 | 1.895 | 35.574 | 102.6 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/3810_25_4_01202020_80.tiff | ./EL/3810_25_4_01202020_20.tiff | ./IV/3810_25_4_01162020.csv | 0 | 0 | 2 | ./RefIV/3810_25_4_01162020.csv | 8.862 | 9.0256 | 8/21/2017 | 10:24 | 1.0117 | 0.98313
263 | 3802 |  | 25 | 4 |  | 16700 |  | multi-Si module |  |  | OE 897 days | 9.41 | 38.97 | 8.84 | 0.93943 | 31.67 | 0.81268 | 280 | 9.446 | 38.67 | 8.972 | 0.94982 | 30.76 | 0.79545 | 276 | 75.6 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 13:19 | PSEL | FLI Proline |  |  |  |  | 7.573 | 40.431 | 25.6 | 1.895 | 35.799 | 102.6 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/3802_25_4_01202020_80.tiff | ./EL/3802_25_4_01202020_20.tiff | ./IV/3802_25_4_01162020.csv | 0 | 0 | 1 | ./RefIV/3802_25_4_01162020.csv | 8.862 | 9.0256 | 2017-02-08 | 10:39 | 1.0111 | 0.9788
264 | 3809 |  | 25 | 4 |  | 16700 |  | multi-Si module |  |  | OE 1263 days | 9.41 | 38.97 | 8.84 | 0.93943 | 31.67 | 0.81268 | 280 | 9.388 | 38.69 | 8.907 | 0.94876 | 30.84 | 0.79711 | 274.7 | 75.6 | 24.8 | back of panel |  | SPIRE | 4600SLP | 2021-04-02 | 13:16 | PSEL | FLI Proline |  |  |  |  | 7.578 | 40.078 | 25.6 | 1.895 | 35.724 | 102.6 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/3809_25_4_02082021_80.tiff | ./EL/3809_25_4_02082021_20.tiff | ./IV/3809_25_4_02042021.csv | 0 | 1 | 2 | ./RefIV/3809_25_4_02042021.csv | 8.862 | 9.0256 | 8/21/2017 | 10:20 | 1.0099 | 0.98084
265 | 3809 |  | 25 | 4 |  | 16700 |  | multi-Si module |  |  | OE 878 days | 9.41 | 38.97 | 8.84 | 0.93943 | 31.67 | 0.81268 | 280 | 9.386 | 38.74 | 8.922 | 0.95056 | 30.98 | 0.79969 | 276.4 | 76 | 24.8 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 12:59 | PSEL | FLI Proline |  |  |  |  | 7.573 | 40.261 | 25.6 | 1.895 | 35.874 | 102.6 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/3809_25_4_01202020_80.tiff | ./EL/3809_25_4_01202020_20.tiff | ./IV/3809_25_4_01162020.csv | 0 | 0 | 2 | ./RefIV/3809_25_4_01162020.csv | 8.862 | 9.0256 | 8/21/2017 | 10:20 | 1.0119 | 0.98402
266 | 3797 |  | 25 | 4 |  | 16700 |  | multi-Si module |  |  | OE 1282 days | 9.41 | 38.97 | 8.84 | 0.93943 | 31.67 | 0.81268 | 280 | 9.456 | 38.52 | 8.951 | 0.94659 | 30.55 | 0.79309 | 273.4 | 75.1 | 25.4 | back of panel |  | SPIRE | 4600SLP | 2021-04-02 | 13:10 | PSEL | FLI Proline |  |  |  |  | 7.578 | 40.266 | 25.6 | 1.895 | 35.724 | 102.6 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/3797_25_4_02082021_80.tiff | ./EL/3797_25_4_02082021_20.tiff | ./IV/3797_25_4_02042021.csv | 0 | 1 | 2 | ./RefIV/3797_25_4_02042021.csv | 8.862 | 9.0256 | 2017-02-08 | 10:57 | 1.0076 | 0.9759
267 | 3797 |  | 25 | 4 |  | 16700 |  | multi-Si module |  |  | OE 897 days | 9.41 | 38.97 | 8.84 | 0.93943 | 31.67 | 0.81268 | 280 | 9.448 | 38.6 | 8.963 | 0.94867 | 30.76 | 0.79689 | 275.7 | 75.6 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 13:13 | PSEL | FLI Proline |  |  |  |  | 7.573 | 40.378 | 25.6 | 1.895 | 35.857 | 102.6 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/3797_25_4_01202020_80.tiff | ./EL/3797_25_4_01202020_20.tiff | ./IV/3797_25_4_01162020.csv | 0 | 0 | 2 | ./RefIV/3797_25_4_01162020.csv | 8.862 | 9.0256 | 2017-02-08 | 10:57 | 1.0098 | 0.98058
268 | 3639 |  | 25 | 4 |  | 16700 |  | multi-Si module |  |  | OE 1288 days | 9.41 | 38.97 | 8.84 | 0.93943 | 31.67 | 0.81268 | 280 | 9.455 | 38.7 | 8.974 | 0.94913 | 30.72 | 0.7938 | 275.7 | 75.3 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2021-04-02 | 13:20 | PSEL | FLI Proline |  |  |  |  | 7.578 | 40.191 | 25.6 | 1.895 | 35.462 | 102.6 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/3639_25_4_02082021_80.tiff | ./EL/3639_25_4_02082021_20.tiff | ./IV/3639_25_4_02042021.csv | 0 | 0 | 1 | ./RefIV/3639_25_4_02042021.csv | 8.862 | 9.0256 | 7/27/2017 | 13:47 | 1.0103 | 0.97677
269 | 3798 |  | 25 | 4 |  | 16700 |  | multi-Si module |  |  | OE 897 days | 9.41 | 38.97 | 8.84 | 0.93943 | 31.67 | 0.81268 | 280 | 9.454 | 38.62 | 8.947 | 0.94637 | 30.66 | 0.79389 | 274.3 | 75.1 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 13:16 | PSEL | FLI Proline |  |  |  |  | 7.573 | 40.378 | 25.6 | 1.895 | 35.837 | 102.6 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/3798_25_4_01202020_80.tiff | ./EL/3798_25_4_01202020_20.tiff | ./IV/3798_25_4_01162020.csv | 0 | 0 | 1 | ./RefIV/3798_25_4_01162020.csv | 8.862 | 9.0256 | 2017-02-08 | 10:53 | 1.0074 | 0.97688
270 | 3803 |  | 25 | 4 |  | 16700 |  | multi-Si module |  |  | OE 897 days | 9.41 | 38.97 | 8.84 | 0.93943 | 31.67 | 0.81268 | 280 | 9.429 | 38.73 | 8.866 | 0.94029 | 30.93 | 0.79861 | 274.2 | 75.1 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 13:17 | PSEL | FLI Proline |  |  |  |  | 7.573 | 40.453 | 25.6 | 1.895 | 35.912 | 102.6 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/3803_25_4_01202020_80.tiff | ./EL/3803_25_4_01202020_20.tiff | ./IV/3803_25_4_01162020.csv | 0 | 0 | 1 | ./RefIV/3803_25_4_01162020.csv | 8.862 | 9.0256 | 2017-02-08 | 10:25 | 1.0009 | 0.98269
271 | 3625 |  | 25 | 4 |  | 16700 |  | multi-Si module |  |  | OE 1023 days | 9.41 | 38.97 | 8.84 | 0.93943 | 31.67 | 0.81268 | 280 | 9.461 | 38.74 | 8.973 | 0.94842 | 30.79 | 0.79479 | 276.3 | 75.4 | 24.8 | back of panel |  | SPIRE | 4600SLP | 2021-04-02 | 13:16 | PSEL | FLI Proline |  |  |  |  | 7.578 | 40.491 | 25.6 | 1.88 | 35.95 | 102.6 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/3625_25_4_02082021_80.tiff | ./EL/3625_25_4_02082021_20.tiff | ./IV/3625_25_4_02042021.csv | 0 | 1 | 2 | ./RefIV/3625_25_4_02042021.csv | 8.862 | 8.862 | 4/18/2018 | 11:00 | 1.0096 | 0.97799
272 | 3625 |  | 25 | 4 |  | 16700 |  | multi-Si module |  |  | OE 638 days | 9.41 | 38.97 | 8.84 | 0.93943 | 31.67 | 0.81268 | 280 | 9.462 | 38.79 | 8.981 | 0.94917 | 30.96 | 0.79814 | 278 | 75.8 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 13:04 | PSEL | FLI Proline |  |  |  |  | 7.573 | 40.528 | 25.6 | 1.895 | 356.175 | 102.6 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/3625_25_4_01202020_80.tiff | ./EL/3625_25_4_01202020_20.tiff | ./IV/3625_25_4_01162020.csv | 0 | 0 | 2 | ./RefIV/3625_25_4_01162020.csv | 8.862 | 8.862 | 4/18/2018 | 11:00 | 1.0104 | 0.98212
273 | 3635 |  | 25 | 4 |  | 16700 |  | multi-Si module |  |  | OE 1288 days | 9.41 | 38.97 | 8.84 | 0.93943 | 31.67 | 0.81268 | 280 | 9.44 | 38.6 | 8.973 | 0.95053 | 30.79 | 0.79767 | 276.2 | 75.8 | 24.8 | back of panel |  | SPIRE | 4600SLP | 2021-04-02 | 13:18 | PSEL | FLI Proline |  |  |  |  | 7.578 | 40.216 | 25.6 | 1.9 | 35.874 | 102.6 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/3635_25_4_02082021_80.tiff | ./EL/3635_25_4_02082021_20.tiff | ./IV/3635_25_4_02042021.csv | 0 | 1 | 2 | ./RefIV/3635_25_4_02042021.csv | 8.862 | 9.0256 | 7/27/2017 | 14:01 | 1.0118 | 0.98153
274 | 3635 |  | 25 | 4 |  | 16700 |  | multi-Si module |  |  | OE 903 days | 9.41 | 38.97 | 8.84 | 0.93943 | 31.67 | 0.81268 | 280 | 9.427 | 38.65 | 8.971 | 0.95163 | 30.97 | 0.80129 | 277.8 | 76.3 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 13:06 | PSEL | FLI Proline |  |  |  |  | 7.573 | 40.228 | 25.6 | 1.895 | 35.874 | 102.6 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/3635_25_4_01202020_80.tiff | ./EL/3635_25_4_01202020_20.tiff | ./IV/3635_25_4_01162020.csv | 0 | 0 | 2 | ./RefIV/3635_25_4_01162020.csv | 8.862 | 9.0256 | 7/27/2017 | 14:01 | 1.013 | 0.98599
275 | 3799 |  | 25 | 4 |  | 16700 |  | multi-Si module |  |  | OE 897 days | 9.41 | 38.97 | 8.84 | 0.93943 | 31.67 | 0.81268 | 280 | 9.442 | 38.69 | 8.964 | 0.94938 | 30.75 | 0.79478 | 275.7 | 75.5 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 13:14 | PSEL | FLI Proline |  |  |  |  | 7.573 | 40.528 | 25.6 | 1.895 | 35.912 | 102.6 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/3799_25_4_01202020_80.tiff | ./EL/3799_25_4_01202020_20.tiff | ./IV/3799_25_4_01162020.csv | 0 | 0 | 1 | ./RefIV/3799_25_4_01162020.csv | 8.862 | 9.0256 | 2017-02-08 | 10:50 | 1.0106 | 0.97798
276 | 3626 |  | 25 | 4 |  | 16700 |  | multi-Si module |  |  | OE 1288 days | 9.41 | 38.97 | 8.84 | 0.93943 | 31.67 | 0.81268 | 280 | 9.438 | 38.75 | 8.969 | 0.95031 | 30.88 | 0.7969 | 277 | 75.7 | 24.8 | back of panel |  | SPIRE | 4600SLP | 2021-04-02 | 13:17 | PSEL | FLI Proline |  |  |  |  | 7.573 | 40.578 | 25.6 | 1.895 | 35.987 | 102.6 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/3626_25_4_02082021_80.tiff | ./EL/3626_25_4_02082021_20.tiff | ./IV/3626_25_4_02042021.csv | 0 | 1 | 2 | ./RefIV/3626_25_4_02042021.csv | 8.862 | 9.0256 | 7/27/2017 | 14:41 | 1.0116 | 0.98059
277 | 3626 |  | 25 | 4 |  | 16700 |  | multi-Si module |  |  | OE 903 days | 9.41 | 38.97 | 8.84 | 0.93943 | 31.67 | 0.81268 | 280 | 9.423 | 38.79 | 8.965 | 0.9514 | 31.03 | 0.79995 | 278.2 | 76.1 | 25 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 13:02 | PSEL | FLI Proline |  |  |  |  | 7.573 | 40.378 | 25.6 | 1.895 | 35.912 | 102.6 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/3626_25_4_01202020_80.tiff | ./EL/3626_25_4_01202020_20.tiff | ./IV/3626_25_4_01162020.csv | 0 | 0 | 2 | ./RefIV/3626_25_4_01162020.csv | 8.862 | 9.0256 | 7/27/2017 | 14:41 | 1.0127 | 0.98434
278 | 3640 |  | 25 | 4 |  | 16700 |  | multi-Si module |  |  | OE 1288 days | 9.41 | 38.97 | 8.84 | 0.93943 | 31.67 | 0.81268 | 280 | 9.451 | 38.7 | 8.966 | 0.94868 | 30.79 | 0.79561 | 276.1 | 75.5 | 24.8 | back of panel |  | SPIRE | 4600SLP | 2021-04-02 | 13:19 | PSEL | FLI Proline |  |  |  |  | 7.573 | 40.16 | 25.6 | 1.895 | 35.95 | 102.6 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/3640_25_4_02082021_80.tiff | ./EL/3640_25_4_02082021_20.tiff | ./IV/3640_25_4_02042021.csv | 0 | 1 | 2 | ./RefIV/3640_25_4_02042021.csv | 8.862 | 9.0256 | 7/27/2017 | 13:43 | 1.0099 | 0.979
279 | 3640 |  | 25 | 4 |  | 16700 |  | multi-Si module |  |  | OE 903 days | 9.41 | 38.97 | 8.84 | 0.93943 | 31.67 | 0.81268 | 280 | 9.438 | 38.74 | 8.965 | 0.94988 | 30.96 | 0.79917 | 277.6 | 75.9 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 13:09 | PSEL | FLI Proline |  |  |  |  | 7.573 | 40.528 | 25.6 | 1.895 | 35.724 | 102.6 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/3640_25_4_01202020_80.tiff | ./EL/3640_25_4_01202020_20.tiff | ./IV/3640_25_4_01162020.csv | 0 | 0 | 2 | ./RefIV/3640_25_4_01162020.csv | 8.862 | 9.0256 | 7/27/2017 | 13:43 | 1.0111 | 0.98339
280 | 3735 |  | 25 | 3 |  | 16683.3 |  | mono-Si module |  |  | OE 1288 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.597 | 39.2 | 9.135 | 0.95186 | 31.63 | 0.80689 | 288.9 | 76.8 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 9:39 | PSEL | FLI Proline |  |  |  |  | 7.578 | 40.094 | 12.8 | 1.895 | 36.775 | 51.2 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/3735_25_3_02082021_80.tiff | ./EL/3735_25_3_02082021_20.tiff | ./IV/3735_25_3_02092021.csv | 0 | 1 | 2 | ./RefIV/3735_25_3_02092021.csv | 8.862 | 9.0256 | 2017-01-08 | 9:39 | 1.0043 | 0.98988
281 | 3735 |  | 25 | 3 |  | 16683.3 |  | mono-Si module |  |  | OE 898 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.596 | 39.28 | 9.135 | 0.95196 | 31.88 | 0.81161 | 291.3 | 77.3 | 25.2 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 14:03 | PSEL | FLI Proline |  |  |  |  | 7.698 | 41.054 | 12.8 | 1.92 | 37 | 51.2 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/3735_25_3_01202020_80.tiff | ./EL/3735_25_3_01202020_20.tiff | ./IV/3735_25_3_01162020.csv | 0 | 0 | 2 | ./RefIV/3735_25_3_01162020.csv | 8.862 | 9.0256 | 2017-01-08 | 9:39 | 1.0044 | 0.99567
282 | 3746 |  | 25 | 3 |  | 16683.3 |  | mono-Si module |  |  | OE 1288 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.553 | 39.31 | 9.132 | 0.95593 | 31.8 | 0.80895 | 290.4 | 77.3 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 9:46 | PSEL | FLI Proline |  |  |  |  | 7.578 | 40.941 | 12.8 | 1.895 | 36.775 | 51.2 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/3746_25_3_02082021_80.tiff | ./EL/3746_25_3_02082021_20.tiff | ./IV/3746_25_3_02092021.csv | 0 | 1 | 2 | ./RefIV/3746_25_3_02092021.csv | 8.862 | 9.0256 | 2017-01-08 | 13:49 | 1.0086 | 0.99241
283 | 3746 |  | 25 | 3 |  | 16683.3 |  | mono-Si module |  |  | OE 898 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.549 | 39.37 | 9.131 | 0.95623 | 31.98 | 0.81229 | 292 | 77.7 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 14:00 | PSEL | FLI Proline |  |  |  |  | 7.698 | 41.166 | 12.8 | 1.925 | 37.113 | 51.2 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/3746_25_3_01202020_80.tiff | ./EL/3746_25_3_01202020_20.tiff | ./IV/3746_25_3_01162020.csv | 0 | 0 | 2 | ./RefIV/3746_25_3_01162020.csv | 8.862 | 9.0256 | 2017-01-08 | 13:49 | 1.0089 | 0.99651
284 | 3720 |  | 25 | 3 |  | 16683.3 |  | mono-Si module |  |  | OE 1288 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.601 | 39.29 | 9.159 | 0.95396 | 31.8 | 0.80937 | 291.3 | 77.2 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 9:42 | PSEL | FLI Proline |  |  |  |  | 7.578 | 40.791 | 12.8 | 1.89 | 36.738 | 51.2 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/3720_25_3_02082021_80.tiff | ./EL/3720_25_3_02082021_20.tiff | ./IV/3720_25_3_02092021.csv | 0 | 0 | 1 | ./RefIV/3720_25_3_02092021.csv | 8.862 | 9.0256 | 2017-01-08 | 10:29 | 1.0065 | 0.99292
285 | 3737 |  | 25 | 3 |  | 16683.3 |  | mono-Si module |  |  | OE 1288 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.595 | 39.24 | 9.132 | 0.95175 | 31.65 | 0.80657 | 289 | 76.8 | 25 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 9:37 | PSEL | FLI Proline |  |  |  |  | 7.573 | 40.941 | 12.8 | 1.895 | 36.85 | 51.2 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/3737_25_3_02082021_80.tiff | ./EL/3737_25_3_02082021_20.tiff | ./IV/3737_25_3_02092021.csv | 0 | 1 | 2 | ./RefIV/3737_25_3_02092021.csv | 8.862 | 9.0256 | 2017-01-08 | 14:15 | 1.0042 | 0.98949
286 | 3737 |  | 25 | 3 |  | 16683.3 |  | mono-Si module |  |  | OE 898 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.597 | 39.35 | 9.143 | 0.95269 | 31.93 | 0.81144 | 292 | 77.3 | 24.6 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 13:56 | PSEL | FLI Proline |  |  |  |  | 7.693 | 41.204 | 12.8 | 1.925 | 37.113 | 51.2 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/3737_25_3_01202020_80.tiff | ./EL/3737_25_3_01202020_20.tiff | ./IV/3737_25_3_01162020.csv | 0 | 0 | 2 | ./RefIV/3737_25_3_01162020.csv | 8.862 | 9.0256 | 2017-01-08 | 14:15 | 1.0052 | 0.99545
287 | 3726 |  | 25 | 3 |  | 16683.3 |  | mono-Si module |  |  | OE 1288 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.597 | 39.28 | 9.147 | 0.95311 | 31.67 | 0.80626 | 289.6 | 76.8 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 9:45 | PSEL | FLI Proline |  |  |  |  | 7.578 | 40.941 | 12.8 | 1.98 | 36.963 | 51.2 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/3726_25_3_02082021_80.tiff | ./EL/3726_25_3_02082021_20.tiff | ./IV/3726_25_3_02092021.csv | 0 | 1 | 2 | ./RefIV/3726_25_3_02092021.csv | 8.862 | 9.0256 | 2017-01-08 | 10:12 | 1.0056 | 0.98911
288 | 3726 |  | 25 | 3 |  | 16683.3 |  | mono-Si module |  |  | OE 898 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.589 | 39.35 | 9.147 | 0.95391 | 31.93 | 0.81144 | 292 | 77.4 | 25.2 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 14:05 | PSEL | FLI Proline |  |  |  |  | 7.698 | 41.166 | 12.8 | 1.925 | 37.113 | 51.2 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/3726_25_3_01202020_80.tiff | ./EL/3726_25_3_01202020_20.tiff | ./IV/3726_25_3_01162020.csv | 0 | 0 | 2 | ./RefIV/3726_25_3_01162020.csv | 8.862 | 9.0256 | 2017-01-08 | 10:12 | 1.0064 | 0.99545
289 | 3738 |  | 25 | 3 |  | 16683.3 |  | mono-Si module |  |  | OE 1288 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.63 | 39.2 | 9.144 | 0.94953 | 31.69 | 0.80842 | 289.7 | 76.8 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 9:49 | PSEL | FLI Proline |  |  |  |  | 7.578 | 40.754 | 12.8 | 1.895 | 36.663 | 51.2 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/3738_25_3_02082021_80.tiff | ./EL/3738_25_3_02082021_20.tiff | ./IV/3738_25_3_02092021.csv | 0 | 1 | 2 | ./RefIV/3738_25_3_02092021.csv | 8.862 | 9.0256 | 2017-01-08 | 14:12 | 1.0018 | 0.99175
290 | 3738 |  | 25 | 3 |  | 16683.3 |  | mono-Si module |  |  | OE 898 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.632 | 39.32 | 9.148 | 0.94975 | 31.95 | 0.81256 | 292.3 | 77.2 | 24.6 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 13:54 | PSEL | FLI Proline |  |  |  |  | 7.693 | 41.091 | 12.8 | 1.925 | 37.075 | 51.2 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/3738_25_3_01202020_80.tiff | ./EL/3738_25_3_01202020_20.tiff | ./IV/3738_25_3_01162020.csv | 0 | 0 | 2 | ./RefIV/3738_25_3_01162020.csv | 8.862 | 9.0256 | 2017-01-08 | 14:12 | 1.0021 | 0.99684
291 | 3811 |  | 25 | 3 |  | 16683.3 |  | mono-Si module |  |  | OE 1268 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.559 | 39.25 | 9.141 | 0.95627 | 31.65 | 0.80637 | 289.3 | 77.1 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 9:44 | PSEL | FLI Proline |  |  |  |  | 7.573 | 40.904 | 12.8 | 1.895 | 36.738 | 51.2 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/3811_25_3_02082021_80.tiff | ./EL/3811_25_3_02082021_20.tiff | ./IV/3811_25_3_02092021.csv | 0 | 1 | 2 | ./RefIV/3811_25_3_02092021.csv | 8.862 | 9.0256 | 8/21/2017 | 10:31 | 1.0089 | 0.98924
292 | 3811 |  | 25 | 3 |  | 16683.3 |  | mono-Si module |  |  | OE 878 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.561 | 39.33 | 9.152 | 0.95722 | 31.93 | 0.81185 | 292.2 | 77.7 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 14:09 | PSEL | FLI Proline |  |  |  |  | 7.698 | 40.378 | 12.8 | 1.895 | 36.437 | 51.2 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/3811_25_3_01202020_80.tiff | ./EL/3811_25_3_01202020_20.tiff | ./IV/3811_25_3_01162020.csv | 0 | 0 | 2 | ./RefIV/3811_25_3_01162020.csv | 8.862 | 9.0256 | 8/21/2017 | 10:31 | 1.0099 | 0.99596
293 | 3754 |  | 25 | 3 |  | 16683.3 |  | mono-Si module |  |  | OE 1288 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.59 | 39.28 | 9.11 | 0.94995 | 31.72 | 0.80754 | 288.9 | 76.7 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 9:38 | PSEL | FLI Proline |  |  |  |  | 7.573 | 40.979 | 12.8 | 1.895 | 36.85 | 51.2 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/3754_25_3_02082021_80.tiff | ./EL/3754_25_3_02082021_20.tiff | ./IV/3754_25_3_02092021.csv | 0 | 1 | 2 | ./RefIV/3754_25_3_02092021.csv | 8.862 | 9.0256 | 2017-01-08 | 13:27 | 1.0023 | 0.99067
294 | 3754 |  | 25 | 3 |  | 16683.3 |  | mono-Si module |  |  | OE 898 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.584 | 39.4 | 9.115 | 0.95106 | 32 | 0.81218 | 291.6 | 77.2 | 24.6 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 13:51 | PSEL | FLI Proline |  |  |  |  | 7.693 | 41.241 | 12.8 | 1.925 | 37.113 | 51.2 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/3754_25_3_01202020_80.tiff | ./EL/3754_25_3_01202020_20.tiff | ./IV/3754_25_3_01162020.csv | 0 | 0 | 2 | ./RefIV/3754_25_3_01162020.csv | 8.862 | 9.0256 | 2017-01-08 | 13:27 | 1.0034 | 0.99637
295 | 3714 |  | 25 | 3 |  | 16683.3 |  | mono-Si module |  |  | OE 1288 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.626 | 39.23 | 9.155 | 0.95107 | 31.64 | 0.80653 | 289.7 | 76.7 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 9:39 | PSEL | FLI Proline |  |  |  |  | 7.578 | 40.829 | 12.8 | 1.895 | 36.738 | 51.2 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/3714_25_3_02082021_80.tiff | ./EL/3714_25_3_02082021_20.tiff | ./IV/3714_25_3_02092021.csv | 0 | 0 | 1 | ./RefIV/3714_25_3_02092021.csv | 8.862 | 9.0256 | 2017-01-08 | 10:54 | 1.0035 | 0.98943
296 | 3742 |  | 25 | 3 |  | 16683.3 |  | mono-Si module |  |  | OE 1288 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.58 | 39.26 | 9.147 | 0.9548 | 31.64 | 0.80591 | 289.4 | 76.9 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 9:48 | PSEL | FLI Proline |  |  |  |  | 7.573 | 40.904 | 12.8 | 1.895 | 36.775 | 51.2 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/3742_25_3_02082021_80.tiff | ./EL/3742_25_3_02082021_20.tiff | ./IV/3742_25_3_02092021.csv | 0 | 1 | 2 | ./RefIV/3742_25_3_02092021.csv | 8.862 | 9.0256 | 2017-01-08 | 14:00 | 1.0074 | 0.98867
297 | 3742 |  | 25 | 3 |  | 16683.3 |  | mono-Si module |  |  | OE 898 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.577 | 39.36 | 9.144 | 0.95479 | 31.91 | 0.81072 | 291.8 | 77.4 | 24.7 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 13:57 | PSEL | FLI Proline |  |  |  |  | 7.693 | 41.166 | 12.8 | 1.92 | 37.113 | 51.2 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/3742_25_3_01202020_80.tiff | ./EL/3742_25_3_01202020_20.tiff | ./IV/3742_25_3_01162020.csv | 0 | 0 | 2 | ./RefIV/3742_25_3_01162020.csv | 8.862 | 9.0256 | 2017-01-08 | 14:00 | 1.0074 | 0.99458
298 | 3744 |  | 25 | 3 |  | 16683.3 |  | mono-Si module |  |  | OE 1288 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.63 | 39.2 | 9.142 | 0.94933 | 31.65 | 0.8074 | 289.4 | 76.7 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 9:47 | PSEL | FLI Proline |  |  |  |  | 7.578 | 40.829 | 12.8 | 1.895 | 36.738 | 51.2 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/3744_25_3_02082021_80.tiff | ./EL/3744_25_3_02082021_20.tiff | ./IV/3744_25_3_02092021.csv | 0 | 1 | 2 | ./RefIV/3744_25_3_02092021.csv | 8.862 | 9.0256 | 2017-01-08 | 13:54 | 1.0016 | 0.9905
299 | 3744 |  | 25 | 3 |  | 16683.3 |  | mono-Si module |  |  | OE 898 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.625 | 39.29 | 9.142 | 0.94982 | 31.9 | 0.81191 | 291.6 | 77.1 | 24.8 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 13:59 | PSEL | FLI Proline |  |  |  |  | 7.693 | 41.129 | 12.8 | 1.92 | 37.075 | 51.2 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/3744_25_3_01202020_80.tiff | ./EL/3744_25_3_01202020_20.tiff | ./IV/3744_25_3_01162020.csv | 0 | 0 | 2 | ./RefIV/3744_25_3_01162020.csv | 8.862 | 9.0256 | 2017-01-08 | 13:54 | 1.0021 | 0.99604
300 | 3747 |  | 25 | 3 |  | 16683.3 |  | mono-Si module |  |  | OE 1288 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.595 | 39.24 | 9.149 | 0.95352 | 31.65 | 0.80657 | 289.6 | 76.9 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 9:50 | PSEL | FLI Proline |  |  |  |  | 7.758 | 40.791 | 12.8 | 1.895 | 36.775 | 51.2 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/3747_25_3_02082021_80.tiff | ./EL/3747_25_3_02082021_20.tiff | ./IV/3747_25_3_02092021.csv | 0 | 1 | 2 | ./RefIV/3747_25_3_02092021.csv | 8.862 | 9.0256 | 2017-01-08 | 13:46 | 1.006 | 0.98949
301 | 3747 |  | 25 | 3 |  | 16683.3 |  | mono-Si module |  |  | OE 898 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.594 | 39.29 | 9.152 | 0.95393 | 31.82 | 0.80988 | 291.2 | 77.2 | 25.3 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 14:01 | PSEL | FLI Proline |  |  |  |  | 7.698 | 41.091 | 12.8 | 1.92 | 36.963 | 51.2 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/3747_25_3_01202020_80.tiff | ./EL/3747_25_3_01202020_20.tiff | ./IV/3747_25_3_01162020.csv | 0 | 0 | 2 | ./RefIV/3747_25_3_01162020.csv | 8.862 | 9.0256 | 2017-01-08 | 13:46 | 1.0065 | 0.99354
302 | 3718 |  | 25 | 3 |  | 16683.3 |  | mono-Si module |  |  | OE 1288 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.594 | 39.23 | 9.15 | 0.95372 | 31.57 | 0.80474 | 288.8 | 76.7 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 9:40 | PSEL | FLI Proline |  |  |  |  | 7.578 | 40.791 | 12.8 | 1.895 | 36.55 | 51.2 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/3718_25_3_02082021_80.tiff | ./EL/3718_25_3_02082021_20.tiff | ./IV/3718_25_3_02092021.csv | 0 | 0 | 1 | ./RefIV/3718_25_3_02092021.csv | 8.862 | 9.0256 | 2017-01-08 | 10:34 | 1.0062 | 0.98724
303 | 3752 |  | 25 | 3 |  | 16683.3 |  | mono-Si module |  |  | OE 898 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.617 | 39.38 | 9.137 | 0.95009 | 31.98 | 0.81209 | 292.2 | 77.2 | 24.5 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 13:53 | PSEL | FLI Proline |  |  |  |  | 7.693 | 41.166 | 12.8 | [7 empty] | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/3752_25_3_01202020_80.tiff |  | ./IV/3752_25_3_01162020.csv | 0 | 0 | 1 | ./RefIV/3752_25_3_01162020.csv | 8.862 | 9.0256 | 2017-01-08 | 13:32 | 1.0024 | 0.99625
304 | 3628 |  | 25 | 4 |  | 16700 |  | multi-Si module |  |  | OE 0 days | 9.41 | 38.97 | 8.84 | 0.93943 | 31.67 | 0.81268 | 280 | 9.444 | 38.71 | 8.968 | 0.9496 | 30.95 | 0.79954 | 277.5 | 75.9 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 13:01 | PSEL | FLI Proline |  |  |  |  | 7.573 | 40.378 | 25.6 | 1.895 | 35.912 | 102.6 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/3628_25_4_01202020_80.tiff | ./EL/3628_25_4_01202020_20.tiff | ./IV/3628_25_4_01162020.csv | 0 | 0 | 1 | ./RefIV/3628_25_4_01162020.csv | 8.862 | 8.862 | 1/16/2020 | 13:01 | 1.0108 | 0.98383
305 | 3734 |  | 25 | 3 |  | 16683.3 |  | mono-Si module |  |  | OE 898 days | 9.77 | 39.76 | 9.26 | 0.9478 | 32.41 | 0.81514 | 300 | 9.583 | 39.31 | 9.144 | 0.95419 | 31.87 | 0.81074 | 291.5 | 77.4 | 25.2 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 14:04 | PSEL | FLI Proline |  |  |  |  | 7.698 | 41.036 | 12.8 | 1.925 | 36.963 | 51.2 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/3734_25_3_01202020_80.tiff | ./EL/3734_25_3_01202020_20.tiff | ./IV/3734_25_3_01162020.csv | 0 | 0 | 1 | ./RefIV/3734_25_3_01162020.csv | 8.862 | 9.0256 | 2017-01-08 | 9:42 | 1.0067 | 0.9946
306 | 3637 |  | 25 | 4 |  | 16700 |  | multi-Si module |  |  | OE 903 days | 9.41 | 38.97 | 8.84 | 0.93943 | 31.67 | 0.81268 | 280 | 9.466 | 38.77 | 8.983 | 0.94898 | 31.02 | 0.8001 | 278.6 | 75.9 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 13:07 | PSEL | FLI Proline |  |  |  |  | 7.573 | 40.416 | 25.6 | 1.895 | 36.025 | 102.6 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/3637_25_4_01202020_80.tiff | ./EL/3637_25_4_01202020_20.tiff | ./IV/3637_25_4_01162020.csv | 0 | 0 | 1 | ./RefIV/3637_25_4_01162020.csv | 8.862 | 9.0256 | 7/27/2017 | 13:54 | 1.0102 | 0.98453
307 | 4554 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 329 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.539 | 47.06 | 9.126 | 0.9567 | 38.31 | 0.81407 | 349.6 | 77.9 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 10:07 | PSEL | FLI Proline |  |  |  |  | 7.623 | 48.785 | 12.8 | 1.905 | 44.131 | 51.25 | [5 empty] | 2021-10-02 |  | 2021-10-02 |  | PSEL | ./EL/4554_12_1_02102021_80.tiff | ./EL/4554_12_1_02102021_20.tiff | ./IV/4554_12_1_02092021.csv | 0 | 0 | 2 | ./RefIV/4554_12_1_02092021.csv | 8.862 | 8.862 | 3/17/2020 | 9:30 | 0.99497 | 1.0008
308 | 4554 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.567 | 47.42 | 9.148 | 0.9562 | 38.87 | 0.8197 | 355.6 | 78.4 | 25.1 | back of panel |  | SPIRE | 4600SLP | 3/17/2020 | 9:30 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.461 | 12.8 | 1.92 | 44.732 | 51.2 |  |  |  |  | 2.69 | 3/23/2020 |  | 3/23/2020 |  | PSEL | ./EL/4554_12_1_03232020_80.tiff | ./EL/4554_12_1_03232020_20.tiff | ./IV/4554_12_1_03172020.csv | 0 | 1 | 2 | ./RefIV/4554_12_1_03172020.csv | 8.862 | 8.862 | 3/17/2020 | 9:30 | 0.99445 | 1.0077
309 | 4352 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 582 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.577 | 47.27 | 9.143 | 0.95468 | 38.58 | 0.81616 | 352.8 | 77.9 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 10:18 | PSEL | FLI Proline |  |  |  |  | 7.628 | 48.935 | 12.8 | 1.906 | 44.561 | 51.25 | [5 empty] | 2021-10-02 |  | 2021-10-02 |  | PSEL | ./EL/4352_12_1_02102021_80.tiff | ./EL/4352_12_1_02102021_20.tiff | ./IV/4352_12_1_02092021.csv | 0 | 0 | 2 | ./RefIV/4352_12_1_02092021.csv | 8.862 | 8.862 | 2019-08-07 | 12:57 | 0.99287 | 1.0033
310 | 4352 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 246 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.62 | 47.61 | 9.198 | 0.95613 | 38.9 | 0.81706 | 357.9 | 78.1 | 25 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 11:07 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.048 | 12.8 | 1.925 | 44.206 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4352_12_1_03112020_80.tiff | ./EL/4352_12_1_03112020_20.tiff | ./IV/4352_12_1_03102020.csv | 0 | 1 | 2 | ./RefIV/4352_12_1_03102020.csv | 8.862 | 8.862 | 2019-08-07 | 12:57 | 0.99438 | 1.0044
311 | 4278 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 571 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.506 | 47.12 | 9.108 | 0.95813 | 38.47 | 0.81643 | 350.4 | 78.2 | 25 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 10:02 | PSEL | FLI Proline |  |  |  |  | 7.623 | 48.785 | 12.8 | 1.905 | 44.169 | 51.25 | [5 empty] | 2021-10-02 |  | 2021-10-02 |  | PSEL | ./EL/4278_12_1_02102021_80.tiff | ./EL/4278_12_1_02102021_20.tiff | ./IV/4278_12_1_02092021.csv | 0 | 0 | 2 | ./RefIV/4278_12_1_02092021.csv | 8.862 | 8.862 | 7/19/2019 | 11:28 | 0.99646 | 1.0037
312 | 4278 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 235 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.567 | 47.21 | 9.17 | 0.9585 | 38.7 | 0.81974 | 354.9 | 78.6 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 11:02 | PSEL | FLI Proline |  |  |  |  | 7.698 | 48.898 | 12.8 | 1.925 | 44.206 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4278_12_1_03112020_80.tiff | ./EL/4278_12_1_03112020_20.tiff | ./IV/4278_12_1_03102020.csv | 0 | 1 | 2 | ./RefIV/4278_12_1_03102020.csv | 8.862 | 8.862 | 7/19/2019 | 11:28 | 0.99684 | 1.0077
313 | 4353 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 582 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.516 | 46.99 | 9.085 | 0.95471 | 38.4 | 0.8172 | 348.8 | 78 | 25.3 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 10:06 | PSEL | FLI Proline |  |  |  |  | 7.623 | 48.71 | 12.8 | 1.9034 | 44.056 | 51.25 | [5 empty] | 2021-10-02 |  | 2021-10-02 |  | PSEL | ./EL/4353_12_1_02102021_80.tiff | ./EL/4353_12_1_02102021_20.tiff | ./IV/4353_12_1_02092021.csv | 0 | 0 | 2 | ./RefIV/4353_12_1_02092021.csv | 8.862 | 8.862 | 2019-08-07 | 12:53 | 0.9929 | 1.0046
314 | 4353 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 246 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.552 | 47.3 | 9.127 | 0.95551 | 38.77 | 0.81966 | 353.8 | 78.3 | 24.6 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 10:52 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.198 | 12.8 | 1.925 | 44.469 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4353_12_1_03112020_80.tiff | ./EL/4353_12_1_03112020_20.tiff | ./IV/4353_12_1_03102020.csv | 0 | 1 | 2 | ./RefIV/4353_12_1_03102020.csv | 8.862 | 8.862 | 2019-08-07 | 12:53 | 0.99373 | 1.0076
315 | 4280 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 571 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.536 | 47.08 | 9.137 | 0.95816 | 38.46 | 0.81691 | 351.4 | 78.3 | 24.7 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 10:14 | PSEL | FLI Proline |  |  |  |  | 7.628 | 48.785 | 12.8 | 1.91 | 44.139 | 51.25 |  |  |  |  | 2.69 | 2021-10-02 |  | 2021-10-02 |  | PSEL | ./EL/4280_12_1_02102021_80.tiff | ./EL/4280_12_1_02102021_20.tiff | ./IV/4280_12_1_02092021.csv | 0 | 0 | 2 | ./RefIV/4280_12_1_02092021.csv | 8.862 | 8.862 | 7/19/2019 | 11:36 | 0.99648 | 1.0042
316 | 4280 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 235 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.604 | 47.25 | 9.186 | 0.95648 | 38.58 | 0.81651 | 354.3 | 78.1 | 25 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 11:03 | PSEL | FLI Proline |  |  |  |  | 7.698 | 48.848 | 12.8 | 1.925 | 44.094 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4280_12_1_03112020_80.tiff | ./EL/4280_12_1_03112020_20.tiff | ./IV/4280_12_1_03102020.csv | 0 | 1 | 2 | ./RefIV/4280_12_1_03102020.csv | 8.862 | 8.862 | 7/19/2019 | 11:36 | 0.99474 | 1.0038
317 | 4279 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 571 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.53 | 47.2 | 9.115 | 0.95645 | 38.63 | 0.81843 | 352.1 | 78.3 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 10:19 | PSEL | FLI Proline |  |  |  |  | 7.623 | 49.048 | 12.8 | 1.905 | 44.507 | 51.25 |  |  |  |  | 2.69 | 2021-10-02 |  | 2021-10-02 |  | PSEL | ./EL/4279_12_1_02102021_80.tiff | ./EL/4279_12_1_02102021_20.tiff | ./IV/4279_12_1_02092021.csv | 0 | 0 | 2 | ./RefIV/4279_12_1_02092021.csv | 8.862 | 8.862 | 7/19/2019 | 11:32 | 0.99471 | 1.0061
318 | 4279 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 235 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.58 | 47.23 | 9.16 | 0.95616 | 38.67 | 0.81876 | 354.2 | 78.3 | 25 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 11:10 | PSEL | FLI Proline |  |  |  |  | 7.698 | 47.997 | 12.8 | 1.925 | 43.456 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4279_12_1_03112020_80.tiff | ./EL/4279_12_1_03112020_20.tiff | ./IV/4279_12_1_03102020.csv | 0 | 1 | 2 | ./RefIV/4279_12_1_03102020.csv | 8.862 | 8.862 | 7/19/2019 | 11:32 | 0.99441 | 1.0065
319 | 4550 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 329 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.555 | 46.79 | 9.132 | 0.95573 | 38.13 | 0.81492 | 348.3 | 77.9 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 10:09 | PSEL | FLI Proline |  |  |  |  | 7.623 | 48.447 | 12.8 | 1.905 | 43.906 | 51.25 | [5 empty] | 2021-10-02 |  | 2021-10-02 |  | PSEL | ./EL/4550_12_1_02102021_80.tiff | ./EL/4550_12_1_02102021_20.tiff | ./IV/4550_12_1_02092021.csv | 0 | 0 | 2 | ./RefIV/4550_12_1_02092021.csv | 8.862 | 8.862 | 3/17/2020 | 9:23 | 0.99396 | 1.0018
320 | 4550 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.574 | 47.22 | 9.159 | 0.95665 | 38.78 | 0.82126 | 355.2 | 78.6 | 25 | back of panel |  | SPIRE | 4600SLP | 3/17/2020 | 9:23 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.198 | 12.8 | 1.925 | 44.544 | 51.2 |  |  |  |  | 2.69 | 3/23/2020 |  | 3/23/2020 |  | PSEL | ./EL/4550_12_1_03232020_80.tiff | ./EL/4550_12_1_03232020_20.tiff | ./IV/4550_12_1_03172020.csv | 0 | 1 | 2 | ./RefIV/4550_12_1_03172020.csv | 8.862 | 8.862 | 3/17/2020 | 9:23 | 0.99492 | 1.0096
321 | 4349 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 582 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.529 | 47.2 | 9.124 | 0.9575 | 38.64 | 0.81864 | 352.6 | 78.4 | 24.8 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 10:12 | PSEL | FLI Proline |  |  |  |  | 7.628 | 48.86 | 12.8 | 1.905 | 44.244 | 51.25 |  |  |  |  | 2.69 | 2021-10-02 |  | 2021-10-02 |  | PSEL | ./EL/4349_12_1_02102021_80.tiff | ./EL/4349_12_1_02102021_20.tiff | ./IV/4349_12_1_02092021.csv | 0 | 0 | 2 | ./RefIV/4349_12_1_02092021.csv | 8.862 | 8.862 | 2019-08-07 | 13:04 | 0.9958 | 1.0064
322 | 4349 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 246 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.576 | 47.32 | 9.158 | 0.95635 | 38.74 | 0.81868 | 354.7 | 78.3 | 24.8 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 10:59 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.123 | 12.8 | 1.92 | 44.319 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4349_12_1_03112020_80.tiff | ./EL/4349_12_1_03112020_20.tiff | ./IV/4349_12_1_03102020.csv | 0 | 1 | 2 | ./RefIV/4349_12_1_03102020.csv | 8.862 | 8.862 | 2019-08-07 | 13:04 | 0.9946 | 1.0064
323 | 4351 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 582 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.537 | 47.3 | 9.134 | 0.95774 | 38.64 | 0.81691 | 352.9 | 78.2 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 10:11 | PSEL | FLI Proline |  |  |  |  | 7.628 | 48.973 | 12.8 | 1.905 | 44.357 | 51.25 | [5 empty] | 2021-10-02 |  | 2021-10-02 |  | PSEL | ./EL/4351_12_1_02102021_80.tiff | ./EL/4351_12_1_02102021_20.tiff | ./IV/4351_12_1_02092021.csv | 0 | 0 | 2 | ./RefIV/4351_12_1_02092021.csv | 8.862 | 8.862 | 2019-08-07 | 12:59 | 0.99605 | 1.0043
324 | 4351 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 246 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.591 | 47.53 | 9.182 | 0.95736 | 38.83 | 0.81696 | 356.5 | 78.2 | 24.7 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 10:57 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.273 | 12.8 | 1.925 | 44.544 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4351_12_1_03112020_80.tiff | ./EL/4351_12_1_03112020_20.tiff | ./IV/4351_12_1_03102020.csv | 0 | 1 | 2 | ./RefIV/4351_12_1_03102020.csv | 8.862 | 8.862 | 2019-08-07 | 12:59 | 0.99565 | 1.0043
325 | 4281 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 571 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.519 | 47.18 | 9.129 | 0.95903 | 38.6 | 0.81814 | 352.4 | 78.5 | 24.6 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 10:13 | PSEL | FLI Proline |  |  |  |  | 7.623 | 48.785 | 12.8 | 1.905 | 44.244 | 51.25 |  |  |  |  | 2.69 | 2021-10-02 |  | 2021-10-02 |  | PSEL | ./EL/4281_12_1_02102021_80.tiff | ./EL/4281_12_1_02102021_20.tiff | ./IV/4281_12_1_02092021.csv | 0 | 0 | 2 | ./RefIV/4281_12_1_02092021.csv | 8.862 | 8.862 | 7/19/2019 | 11:39 | 0.99739 | 1.0058
326 | 4281 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 235 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.566 | 47.23 | 9.165 | 0.95808 | 38.68 | 0.81897 | 354.5 | 78.5 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 11:00 | PSEL | FLI Proline |  |  |  |  | 7.698 | 48.785 | 12.8 | 1.925 | 44.131 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4281_12_1_03112020_80.tiff | ./EL/4281_12_1_03112020_20.tiff | ./IV/4281_12_1_03102020.csv | 0 | 1 | 2 | ./RefIV/4281_12_1_03102020.csv | 8.862 | 8.862 | 7/19/2019 | 11:39 | 0.9964 | 1.0068
327 | 4355 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 582 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.53 | 47.21 | 9.108 | 0.95572 | 38.51 | 0.81572 | 350.8 | 78 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 10:00 | PSEL | FLI Proline |  |  |  |  | 7.628 | 48.898 | 12.8 | 1.905 | 44.206 | 51.25 | [5 empty] | 2021-10-02 |  | 2021-10-02 |  | PSEL | ./EL/4355_12_1_02102021_80.tiff | ./EL/4355_12_1_02102021_20.tiff | ./IV/4355_12_1_02092021.csv | 0 | 0 | 2 | ./RefIV/4355_12_1_02092021.csv | 8.862 | 8.862 | 2019-08-07 | 12:42 | 0.99395 | 1.0028
328 | 4355 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 246 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.583 | 47.33 | 9.17 | 0.9569 | 38.74 | 0.81851 | 355.3 | 78.3 | 24.7 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 10:55 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.161 | 12.8 | 1.92 | 44.469 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4355_12_1_03112020_80.tiff | ./EL/4355_12_1_03112020_20.tiff | ./IV/4355_12_1_03102020.csv | 0 | 1 | 2 | ./RefIV/4355_12_1_03102020.csv | 8.862 | 8.862 | 2019-08-07 | 12:42 | 0.99518 | 1.0062
329 | 4350 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 582 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.532 | 47.16 | 9.124 | 0.9572 | 38.63 | 0.81913 | 352.5 | 78.4 | 25 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 10:16 | PSEL | FLI Proline |  |  |  |  | 7.619 | 49.852 | 12.8 | 1.905 | 44.394 | 51.25 |  |  |  |  | 2.69 | 2021-10-02 |  | 2021-10-02 |  | PSEL | ./EL/4350_12_1_02102021_80.tiff | ./EL/4350_12_1_02102021_20.tiff | ./IV/4350_12_1_02092021.csv | 0 | 0 | 2 | ./RefIV/4350_12_1_02092021.csv | 8.862 | 8.862 | 2019-08-07 | 13:02 | 0.99548 | 1.007
330 | 4350 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 246 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.566 | 47.26 | 9.16 | 0.95756 | 38.7 | 0.81887 | 354.5 | 78.4 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 11:06 | PSEL | FLI Proline |  |  |  |  | 7.698 | 48.71 | 12.8 | 1.925 | 43.944 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4350_12_1_03112020_80.tiff | ./EL/4350_12_1_03112020_20.tiff | ./IV/4350_12_1_03102020.csv | 0 | 1 | 2 | ./RefIV/4350_12_1_03102020.csv | 8.862 | 8.862 | 2019-08-07 | 13:02 | 0.99586 | 1.0067
331 | 4282 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 571 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.539 | 47.09 | 9.119 | 0.95597 | 38.46 | 0.81673 | 350.7 | 78.1 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 10:15 | PSEL | FLI Proline |  |  |  |  | 7.628 | 48.785 | 12.8 | 1.905 | 44.169 | 51.25 |  |  |  |  | 2.69 | 2021-10-02 |  | 2021-10-02 |  | PSEL | ./EL/4282_12_1_02102021_80.tiff | ./EL/4282_12_1_02102021_20.tiff | ./IV/4282_12_1_02092021.csv | 0 | 0 | 2 | ./RefIV/4282_12_1_02092021.csv | 8.862 | 8.862 | 7/19/2019 | 11:43 | 0.99421 | 1.004
332 | 4282 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 235 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.577 | 47.29 | 9.17 | 0.9575 | 38.66 | 0.81751 | 354.5 | 78.3 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 11:04 | PSEL | FLI Proline |  |  |  |  | 7.698 | 48.793 | 12.8 | 1.92 | 44.019 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4282_12_1_03112020_80.tiff | ./EL/4282_12_1_03112020_20.tiff | ./IV/4282_12_1_03102020.csv | 0 | 1 | 2 | ./RefIV/4282_12_1_03102020.csv | 8.862 | 8.862 | 7/19/2019 | 11:43 | 0.9958 | 1.005
333 | 4539 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.571 | 47.38 | 9.152 | 0.95622 | 38.99 | 0.82292 | 356.8 | 78.7 | 25 | back of panel |  | SPIRE | 4600SLP | 3/17/2020 | 8:56 | PSEL | FLI Proline |  |  |  |  | 7.698 | 48.935 | 12.8 | 1.92 | 44.206 | 51.2 |  |  |  |  | 2.69 | 3/23/2020 |  | 3/23/2020 |  | PSEL | ./EL/4539_12_1_03232020_80.tiff | ./EL/4539_12_1_03232020_20.tiff | ./IV/4539_12_1_03172020.csv | 0 | 0 | 1 | ./RefIV/4539_12_1_03172020.csv | 8.862 | 8.862 | 3/17/2020 | 8:56 | 0.99447 | 1.0116
334 | 4533 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.616 | 47.41 | 9.199 | 0.95663 | 39.05 | 0.82367 | 359.2 | 78.8 | 25 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 14:52 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.611 | 12.8 | 1.92 | 45.07 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4533_12_1_03112020_80.tiff | ./EL/4533_12_1_03112020_20.tiff | ./IV/4533_12_1_03102020.csv | 0 | 0 | 1 | ./RefIV/4533_12_1_03102020.csv | 8.862 | 8.862 | 2020-10-03 | 14:52 | 0.9949 | 1.0126
335 | 4529 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.62 | 47.4 | 9.204 | 0.95676 | 39 | 0.82278 | 359 | 78.7 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 14:39 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.461 | 12.8 | 1.925 | 44.957 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4529_12_1_03112020_80.tiff | ./EL/4529_12_1_03112020_20.tiff | ./IV/4529_12_1_03102020.csv | 0 | 1 | 2 | ./RefIV/4529_12_1_03102020.csv | 8.862 | 8.862 | 2020-10-03 | 14:39 | 0.99503 | 1.0115
336 | 4529 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 329 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.558 | 47.06 | 9.133 | 0.95553 | 38.47 | 0.81747 | 351.3 | 78.1 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2021-02-02 | 9:57 | PSEL | FLI Proline |  |  |  |  | 7.638 | 48.485 | 12.8 | 1.91 | 43.906 | 51.2 |  |  |  |  | 2.76 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/4529_12_1_02082021_80.tiff | ./EL/4529_12_1_02082021_20.tiff | ./IV/4529_12_1_02022021.csv | 0 | 0 | 2 | ./RefIV/4529_12_1_02022021.csv | 8.862 | 8.862 | 2020-10-03 | 14:39 | 0.99376 | 1.0049
337 | 4538 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.622 | 47.54 | 9.213 | 0.95749 | 39.16 | 0.82373 | 360.8 | 78.9 | 24.6 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 15:07 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.161 | 12.8 | 1.92 | 44.657 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4538_12_1_03112020_80.tiff | ./EL/4538_12_1_03112020_20.tiff | ./IV/4538_12_1_03102020.csv | 0 | 0 | 1 | ./RefIV/4538_12_1_03102020.csv | 8.862 | 8.862 | 2020-10-03 | 15:07 | 0.99579 | 1.0126
338 | 4527 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.617 | 47.39 | 9.207 | 0.95737 | 38.96 | 0.82211 | 358.7 | 78.7 | 25.3 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 14:36 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.423 | 12.8 | 1.925 | 44.919 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4527_12_1_03112020_80.tiff | ./EL/4527_12_1_03112020_20.tiff | ./IV/4527_12_1_03102020.csv | 0 | 0 | 1 | ./RefIV/4527_12_1_03102020.csv | 8.862 | 8.862 | 2020-10-03 | 14:36 | 0.99566 | 1.0106
339 | 4542 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.574 | 47.36 | 9.145 | 0.95519 | 38.95 | 0.82242 | 356.2 | 78.6 | 25 | back of panel |  | SPIRE | 4600SLP | 3/17/2020 | 9:07 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.348 | 12.8 | 1.925 | 44.732 | 51.2 |  |  |  |  | 2.69 | 3/23/2020 |  | 3/23/2020 |  | PSEL | ./EL/4542_12_1_03232020_80.tiff | ./EL/4542_12_1_03232020_20.tiff | ./IV/4542_12_1_03172020.csv | 0 | 0 | 1 | ./RefIV/4542_12_1_03172020.csv | 8.862 | 8.862 | 3/17/2020 | 9:07 | 0.9934 | 1.011
340 | 4509 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.604 | 47.4 | 9.202 | 0.95814 | 38.87 | 0.82004 | 357.7 | 78.6 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 13:43 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.648 | 12.8 | 1.925 | 45.032 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4509_12_1_03112020_80.tiff | ./EL/4509_12_1_03112020_20.tiff | ./IV/4509_12_1_03102020.csv | 0 | 0 | 1 | ./RefIV/4509_12_1_03102020.csv | 8.862 | 8.862 | 2020-10-03 | 13:43 | 0.99647 | 1.0081
341 | 4516 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.627 | 47.42 | 9.18 | 0.95357 | 39.04 | 0.82328 | 358.4 | 78.5 | 25.3 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 14:04 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.648 | 12.8 | 1.925 | 45.107 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4516_12_1_03112020_80.tiff | ./EL/4516_12_1_03112020_20.tiff | ./IV/4516_12_1_03102020.csv | 0 | 0 | 1 | ./RefIV/4516_12_1_03102020.csv | 8.862 | 8.862 | 2020-10-03 | 14:04 | 0.99171 | 1.0121
342 | 4548 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.57 | 47.46 | 9.16 | 0.95716 | 39.01 | 0.82196 | 357.3 | 78.7 | 24.9 | back of panel |  | SPIRE | 4600SLP | 3/17/2020 | 9:18 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.401 | 12.8 | 1.925 | 44.807 | 51.2 |  |  |  |  | 2.69 | 3/23/2020 |  | 3/23/2020 |  | PSEL | ./EL/4548_12_1_03232020_80.tiff | ./EL/4548_12_1_03232020_20.tiff | ./IV/4548_12_1_03172020.csv | 0 | 1 | 2 | ./RefIV/4548_12_1_03172020.csv | 8.862 | 8.862 | 3/17/2020 | 9:18 | 0.99544 | 1.0105
343 | 4548 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 322 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.554 | 47.09 | 9.139 | 0.95656 | 38.43 | 0.8161 | 351.2 | 78 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-02-02 | 10:10 | PSEL | FLI Proline |  |  |  |  | 7.638 | 48.072 | 12.8 | 1.91 | 43.869 | 51.2 |  |  |  |  | 2.76 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/4548_12_1_02082021_80.tiff | ./EL/4548_12_1_02082021_20.tiff | ./IV/4548_12_1_02022021.csv | 0 | 0 | 2 | ./RefIV/4548_12_1_02022021.csv | 8.862 | 8.862 | 3/17/2020 | 9:18 | 0.99483 | 1.0033
344 | 4555 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.548 | 47.36 | 9.143 | 0.95758 | 39 | 0.82348 | 356.5 | 78.9 | 24.9 | back of panel |  | SPIRE | 4600SLP | 3/17/2020 | 9:34 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.311 | 12.8 | 1.92 | 44.844 | 51.2 |  |  |  |  | 2.69 | 3/23/2020 |  | 3/23/2020 |  | PSEL | ./EL/4555_12_1_03232020_80.tiff | ./EL/4555_12_1_03232020_20.tiff | ./IV/4555_12_1_03172020.csv | 0 | 0 | 1 | ./RefIV/4555_12_1_03172020.csv | 8.862 | 8.862 | 3/17/2020 | 9:34 | 0.99589 | 1.0123
345 | 4513 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.603 | 47.38 | 9.185 | 0.95647 | 38.79 | 0.8187 | 356.3 | 78.3 | 25 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 13:58 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.611 | 12.8 | 1.93 | 44.882 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4513_12_1_03112020_80.tiff | ./EL/4513_12_1_03112020_20.tiff | ./IV/4513_12_1_03102020.csv | 0 | 0 | 1 | ./RefIV/4513_12_1_03102020.csv | 8.862 | 8.862 | 2020-10-03 | 13:58 | 0.99473 | 1.0064
346 | 4511 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.608 | 47.49 | 9.215 | 0.9591 | 39.06 | 0.82249 | 359.9 | 78.9 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 13:53 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.686 | 12.8 | 1.925 | 45.182 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4511_12_1_03112020_80.tiff | ./EL/4511_12_1_03112020_20.tiff | ./IV/4511_12_1_03102020.csv | 0 | 0 | 1 | ./RefIV/4511_12_1_03102020.csv | 8.862 | 8.862 | 2020-10-03 | 13:53 | 0.99746 | 1.0111
347 | 4556 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.57 | 47.35 | 9.145 | 0.95559 | 39.01 | 0.82386 | 356.7 | 78.7 | 24.9 | back of panel |  | SPIRE | 4600SLP | 3/17/2020 | 9:36 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.461 | 12.8 | 1.92 | 44.882 | 51.2 |  |  |  |  | 2.69 | 3/23/2020 |  | 3/23/2020 |  | PSEL | ./EL/4556_12_1_03232020_80.tiff | ./EL/4556_12_1_03232020_20.tiff | ./IV/4556_12_1_03172020.csv | 0 | 0 | 1 | ./RefIV/4556_12_1_03172020.csv | 8.862 | 8.862 | 3/17/2020 | 9:36 | 0.99381 | 1.0128
348 | 4514 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.603 | 47.34 | 9.193 | 0.95731 | 38.96 | 0.82298 | 358.2 | 78.8 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 14:00 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.498 | 12.8 | 1.925 | 44.882 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4514_12_1_03112020_80.tiff | ./EL/4514_12_1_03112020_20.tiff | ./IV/4514_12_1_03102020.csv | 0 | 0 | 1 | ./RefIV/4514_12_1_03102020.csv | 8.862 | 8.862 | 2020-10-03 | 14:00 | 0.9956 | 1.0117
349 | 4535 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.614 | 47.37 | 9.202 | 0.95715 | 38.96 | 0.82246 | 358.5 | 78.7 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 14:57 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.686 | 12.8 | 1.925 | 45.07 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4535_12_1_03112020_80.tiff | ./EL/4535_12_1_03112020_20.tiff | ./IV/4535_12_1_03102020.csv | 0 | 0 | 1 | ./RefIV/4535_12_1_03102020.csv | 8.862 | 8.862 | 2020-10-03 | 14:57 | 0.99543 | 1.0111
350 | 4536 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.623 | 47.39 | 9.2 | 0.95604 | 38.89 | 0.82064 | 357.8 | 78.5 | 25.3 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 14:59 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.799 | 12.8 | 1.925 | 45.182 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4536_12_1_03112020_80.tiff | ./EL/4536_12_1_03112020_20.tiff | ./IV/4536_12_1_03102020.csv | 0 | 0 | 1 | ./RefIV/4536_12_1_03102020.csv | 8.862 | 8.862 | 2020-10-03 | 14:59 | 0.99428 | 1.0088
351 | 4518 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.614 | 47.42 | 9.205 | 0.95746 | 38.99 | 0.82223 | 358.9 | 78.7 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 14:09 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.799 | 12.8 | 1.925 | 45.07 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4518_12_1_03112020_80.tiff | ./EL/4518_12_1_03112020_20.tiff | ./IV/4518_12_1_03102020.csv | 0 | 0 | 1 | ./RefIV/4518_12_1_03102020.csv | 8.862 | 8.862 | 2020-10-03 | 14:09 | 0.99576 | 1.0108
352 | 4557 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.557 | 47.42 | 9.161 | 0.95856 | 39.07 | 0.82391 | 357.9 | 79 | 25 | back of panel |  | SPIRE | 4600SLP | 3/17/2020 | 9:37 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.423 | 12.8 | 1.925 | 44.919 | 51.2 |  |  |  |  | 2.69 | 3/23/2020 |  | 3/23/2020 |  | PSEL | ./EL/4557_12_1_03232020_80.tiff | ./EL/4557_12_1_03232020_20.tiff | ./IV/4557_12_1_03172020.csv | 0 | 0 | 1 | ./RefIV/4557_12_1_03172020.csv | 8.862 | 8.862 | 3/17/2020 | 9:37 | 0.99691 | 1.0129
353 | 4519 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.594 | 47.39 | 9.185 | 0.95737 | 39.04 | 0.8238 | 358.6 | 78.9 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 14:10 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.611 | 12.8 | 1.925 | 44.995 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4519_12_1_03112020_80.tiff | ./EL/4519_12_1_03112020_20.tiff | ./IV/4519_12_1_03102020.csv | 0 | 1 | 2 | ./RefIV/4519_12_1_03102020.csv | 8.862 | 8.862 | 2020-10-03 | 14:10 | 0.99566 | 1.0127
354 | 4519 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 329 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.51 | 47 | 9.111 | 0.95804 | 38.52 | 0.81957 | 350.9 | 78.5 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2021-02-02 | 9:58 | PSEL | FLI Proline | [7 empty] | 7.638 | 48.447 | 12.8 |  |  |  |  | 2.76 | 2021-08-02 |  | 2021-08-02 |  | PSEL |  | ./EL/4519_12_1_02082021_20.tiff | ./IV/4519_12_1_02022021.csv | 0 | 0 | 2 | ./RefIV/4519_12_1_02022021.csv | 8.862 | 8.862 | 2020-10-03 | 14:10 | 0.99637 | 1.0075
355 | 4517 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.625 | 47.36 | 9.206 | 0.95647 | 38.96 | 0.82264 | 358.7 | 78.7 | 25.3 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 14:06 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.536 | 12.8 | 1.925 | 45.032 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4517_12_1_03112020_80.tiff | ./EL/4517_12_1_03112020_20.tiff | ./IV/4517_12_1_03102020.csv | 0 | 0 | 1 | ./RefIV/4517_12_1_03102020.csv | 8.862 | 8.862 | 2020-10-03 | 14:06 | 0.99473 | 1.0113
356 | 4524 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.62 | 47.46 | 9.208 | 0.95717 | 39.09 | 0.82364 | 360 | 78.8 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 14:28 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.498 | 12.8 | 1.925 | 44.995 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4524_12_1_03112020_80.tiff | ./EL/4524_12_1_03112020_20.tiff | ./IV/4524_12_1_03102020.csv | 0 | 1 | 2 | ./RefIV/4524_12_1_03102020.csv | 8.862 | 8.862 | 2020-10-03 | 14:28 | 0.99546 | 1.0125
357 | 4524 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 329 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.538 | 47.1 | 9.133 | 0.95754 | 38.55 | 0.81847 | 352.1 | 78.4 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-02-02 | 10:01 | PSEL | FLI Proline |  |  |  |  | 7.633 | 48.523 | 12.8 | 1.91 | 43.981 | 51.2 |  |  |  |  | 2.76 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/4524_12_1_02082021_80.tiff | ./EL/4524_12_1_02082021_20.tiff | ./IV/4524_12_1_02022021.csv | 0 | 0 | 2 | ./RefIV/4524_12_1_02022021.csv | 8.862 | 8.862 | 2020-10-03 | 14:28 | 0.99584 | 1.0062
358 | 4530 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.623 | 47.46 | 9.205 | 0.95656 | 39 | 0.82174 | 359 | 78.6 | 25 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 14:41 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.536 | 12.8 | 1.925 | 44.919 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4530_12_1_03112020_80.tiff | ./EL/4530_12_1_03112020_20.tiff | ./IV/4530_12_1_03102020.csv | 0 | 0 | 1 | ./RefIV/4530_12_1_03102020.csv | 8.862 | 8.862 | 2020-10-03 | 14:41 | 0.99482 | 1.0102
359 | 4521 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.611 | 47.51 | 9.215 | 0.9588 | 39.17 | 0.82446 | 360.9 | 79 | 24.7 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 14:14 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.611 | 12.8 | 1.92 | 45.107 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4521_12_1_03112020_80.tiff | ./EL/4521_12_1_03112020_20.tiff | ./IV/4521_12_1_03102020.csv | 0 | 0 | 1 | ./RefIV/4521_12_1_03102020.csv | 8.862 | 8.862 | 2020-10-03 | 14:14 | 0.99715 | 1.0135
360 | 4354 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 246 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.577 | 47.39 | 9.184 | 0.95896 | 38.74 | 0.81747 | 355.8 | 78.4 | 25 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 11:09 | PSEL | FLI Proline |  |  |  |  | 7.698 | 48.935 | 12.8 | 1.925 | 44.2 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4354_12_1_03112020_80.tiff | ./EL/4354_12_1_03112020_20.tiff | ./IV/4354_12_1_03102020.csv | 0 | 0 | 1 | ./RefIV/4354_12_1_03102020.csv | 8.862 | 8.862 | 2019-08-07 | 12:49 | 0.99732 | 1.0049
361 | 4522 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.619 | 47.26 | 9.192 | 0.95561 | 38.77 | 0.82036 | 356.4 | 78.4 | 24.7 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 14:16 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.611 | 12.8 | 1.925 | 44.995 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4522_12_1_03112020_80.tiff | ./EL/4522_12_1_03112020_20.tiff | ./IV/4522_12_1_03102020.csv | 0 | 0 | 1 | ./RefIV/4522_12_1_03102020.csv | 8.862 | 8.862 | 2020-10-03 | 14:16 | 0.99383 | 1.0085
362 | 4525 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.618 | 47.39 | 9.193 | 0.95581 | 39.01 | 0.82317 | 358.7 | 78.7 | 25.3 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 14:32 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.348 | 12.8 | 1.925 | 44.882 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4525_12_1_03112020_80.tiff | ./EL/4525_12_1_03112020_20.tiff | ./IV/4525_12_1_03102020.csv | 0 | 1 | 2 | ./RefIV/4525_12_1_03102020.csv | 8.862 | 8.862 | 2020-10-03 | 14:32 | 0.99404 | 1.0119
363 | 4525 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 329 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.542 | 47.03 | 9.123 | 0.95609 | 38.49 | 0.81841 | 351.1 | 78.2 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-02-02 | 10:07 | PSEL | FLI Proline |  |  |  |  | 7.643 | 48.41 | 12.8 | 1.91 | 43.869 | 51.2 |  |  |  |  | 2.76 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/4525_12_1_02082021_80.tiff | ./EL/4525_12_1_02082021_20.tiff | ./IV/4525_12_1_02022021.csv | 0 | 0 | 2 | ./RefIV/4525_12_1_02022021.csv | 8.862 | 8.862 | 2020-10-03 | 14:32 | 0.99433 | 1.0061
364 | 4546 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.574 | 47.51 | 9.154 | 0.95613 | 39.17 | 0.82446 | 358.6 | 78.8 | 24.9 | back of panel |  | SPIRE | 4600SLP | 3/17/2020 | 9:14 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.386 | 12.8 | 1.925 | 44.844 | 51.2 |  |  |  |  | 2.69 | 3/23/2020 |  | 3/23/2020 |  | PSEL | ./EL/4546_12_1_03232020_80.tiff | ./EL/4546_12_1_03232020_20.tiff | ./IV/4546_12_1_03172020.csv | 0 | 0 | 1 | ./RefIV/4546_12_1_03172020.csv | 8.862 | 8.862 | 3/17/2020 | 9:14 | 0.99438 | 1.0135
365 | 4558 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.531 | 47.36 | 9.136 | 0.95856 | 38.98 | 0.82306 | 356.1 | 78.9 | 25.1 | back of panel |  | SPIRE | 4600SLP | 3/17/2020 | 9:40 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.461 | 12.8 | 1.925 | 44.882 | 51.2 |  |  |  |  | 2.69 | 3/23/2020 |  | 3/23/2020 |  | PSEL | ./EL/4558_12_1_03232020_80.tiff | ./EL/4558_12_1_03232020_20.tiff | ./IV/4558_12_1_03172020.csv | 0 | 1 | 2 | ./RefIV/4558_12_1_03172020.csv | 8.862 | 8.862 | 3/17/2020 | 9:40 | 0.9969 | 1.0118
366 | 4558 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 322 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.515 | 46.95 | 9.105 | 0.95691 | 38.4 | 0.81789 | 349.7 | 78.3 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-02-02 | 10:08 | PSEL | FLI Proline |  |  |  |  | 7.638 | 48.372 | 12.8 | 1.91 | 43.756 | 51.2 |  |  |  |  | 2.76 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/4558_12_1_02082021_80.tiff | ./EL/4558_12_1_02082021_20.tiff | ./IV/4558_12_1_02022021.csv | 0 | 0 | 2 | ./RefIV/4558_12_1_02022021.csv | 8.862 | 8.862 | 3/17/2020 | 9:40 | 0.99519 | 1.0055
367 | 4551 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.561 | 47.38 | 9.145 | 0.95649 | 38.92 | 0.82144 | 355.9 | 78.6 | 24.9 | back of panel |  | SPIRE | 4600SLP | 3/17/2020 | 9:25 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.461 | 12.8 | 1.93 | 44.807 | 51.2 |  |  |  |  | 2.69 | 3/23/2020 |  | 3/23/2020 |  | PSEL | ./EL/4551_12_1_03232020_80.tiff | ./EL/4551_12_1_03232020_20.tiff | ./IV/4551_12_1_03172020.csv | 0 | 1 | 2 | ./RefIV/4551_12_1_03172020.csv | 8.862 | 8.862 | 3/17/2020 | 9:25 | 0.99475 | 1.0098
368 | 4551 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 322 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.541 | 46.99 | 9.121 | 0.95598 | 38.33 | 0.81571 | 349.6 | 78 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-02-02 | 10:09 | PSEL | FLI Proline |  |  |  |  | 7.643 | 48.523 | 12.8 | 1.91 | 43.906 | 51.2 |  |  |  |  | 2.76 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/4551_12_1_02082021_80.tiff | ./EL/4551_12_1_02082021_20.tiff | ./IV/4551_12_1_02022021.csv | 0 | 0 | 2 | ./RefIV/4551_12_1_02022021.csv | 8.862 | 8.862 | 3/17/2020 | 9:25 | 0.99422 | 1.0028
369 | 4541 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.549 | 47.4 | 9.144 | 0.95759 | 39 | 0.82278 | 356.7 | 78.8 | 24.9 | back of panel |  | SPIRE | 4600SLP | 3/17/2020 | 9:05 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.236 | 12.8 | 1.925 | 44.694 | 51.2 |  |  |  |  | 2.69 | 3/23/2020 |  | 3/23/2020 |  | PSEL | ./EL/4541_12_1_03232020_80.tiff | ./EL/4541_12_1_03232020_20.tiff | ./IV/4541_12_1_03172020.csv | 0 | 1 | 2 | ./RefIV/4541_12_1_03172020.csv | 8.862 | 8.862 | 3/17/2020 | 9:05 | 0.99589 | 1.0115
370 | 4541 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 322 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.529 | 47.01 | 9.111 | 0.95613 | 38.38 | 0.81642 | 349.7 | 78.1 | 25 | back of panel |  | SPIRE | 4600SLP | 2021-02-02 | 10:00 | PSEL | FLI Proline |  |  |  |  | 7.638 | 48.335 | 12.8 | 1.91 | 43.756 | 51.2 |  |  |  |  | 2.76 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/4541_12_1_02082021_80.tiff | ./EL/4541_12_1_02082021_20.tiff | ./IV/4541_12_1_02022021.csv | 0 | 0 | 2 | ./RefIV/4541_12_1_02022021.csv | 8.862 | 8.862 | 3/17/2020 | 9:05 | 0.99438 | 1.0036
371 | 4510 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.604 | 47.53 | 9.203 | 0.95825 | 39.08 | 0.82222 | 359.7 | 78.8 | 25 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 13:49 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.686 | 12.8 | 1.92 | 45.145 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4510_12_1_03112020_80.tiff | ./EL/4510_12_1_03112020_20.tiff | ./IV/4510_12_1_03102020.csv | 0 | 0 | 1 | ./RefIV/4510_12_1_03102020.csv | 8.862 | 8.862 | 2020-10-03 | 13:49 | 0.99658 | 1.0108
372 | 4547 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.568 | 47.37 | 9.153 | 0.95663 | 38.96 | 0.82246 | 356.7 | 78.7 | 24.9 | back of panel |  | SPIRE | 4600SLP | 3/17/2020 | 9:16 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.348 | 12.8 | 1.92 | 44.732 | 51.2 |  |  |  |  | 2.69 | 3/23/2020 |  | 3/23/2020 |  | PSEL | ./EL/4547_12_1_03232020_80.tiff | ./EL/4547_12_1_03232020_20.tiff | ./IV/4547_12_1_03172020.csv | 0 | 0 | 1 | ./RefIV/4547_12_1_03172020.csv | 8.862 | 8.862 | 3/17/2020 | 9:16 | 0.99489 | 1.0111
373 | 4540 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.544 | 47.42 | 9.155 | 0.95924 | 39.05 | 0.82349 | 357.5 | 79 | 24.9 | back of panel |  | SPIRE | 4600SLP | 3/17/2020 | 9:03 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.348 | 12.8 | 1.925 | 44.694 | 51.2 |  |  |  |  | 2.69 | 3/23/2020 |  | 3/23/2020 |  | PSEL | ./EL/4540_12_1_03232020_80.tiff | ./EL/4540_12_1_03232020_20.tiff | ./IV/4540_12_1_03172020.csv | 0 | 0 | 1 | ./RefIV/4540_12_1_03172020.csv | 8.862 | 8.862 | 3/17/2020 | 9:03 | 0.99761 | 1.0123
374 | 4512 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.619 | 47.32 | 9.198 | 0.95623 | 38.92 | 0.82249 | 358 | 78.6 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 13:56 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.611 | 12.8 | 1.925 | 44.995 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4512_12_1_03112020_80.tiff | ./EL/4512_12_1_03112020_20.tiff | ./IV/4512_12_1_03102020.csv | 0 | 1 | 2 | ./RefIV/4512_12_1_03102020.csv | 8.862 | 8.862 | 2020-10-03 | 13:56 | 0.99448 | 1.0111
375 | 4512 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 329 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.54 | 46.93 | 9.126 | 0.9566 | 38.41 | 0.81845 | 350.5 | 78.3 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-02-02 | 10:04 | PSEL | FLI Proline |  |  |  |  | 7.643 | 48.335 | 12.8 | 1.91 | 43.794 | 51.2 |  |  |  |  | 2.76 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/4512_12_1_02082021_80.tiff | ./EL/4512_12_1_02082021_20.tiff | ./IV/4512_12_1_02022021.csv | 0 | 0 | 2 | ./RefIV/4512_12_1_02022021.csv | 8.862 | 8.862 | 2020-10-03 | 13:56 | 0.99487 | 1.0061
376 | 4549 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.572 | 47.43 | 9.155 | 0.95644 | 39.08 | 0.82395 | 357.8 | 78.8 | 25 | back of panel |  | SPIRE | 4600SLP | 3/17/2020 | 9:20 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.423 | 12.8 | 1.92 | 49.894 | 51.2 |  |  |  |  | 2.69 | 3/23/2020 |  | 3/23/2020 |  | PSEL | ./EL/4549_12_1_03232020_80.tiff | ./EL/4549_12_1_03232020_20.tiff | ./IV/4549_12_1_03172020.csv | 0 | 0 | 1 | ./RefIV/4549_12_1_03172020.csv | 8.862 | 8.862 | 3/17/2020 | 9:20 | 0.99469 | 1.0129
377 | 4531 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.619 | 47.51 | 9.203 | 0.95675 | 39.18 | 0.82467 | 360.6 | 78.9 | 24.8 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 14:44 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.686 | 12.8 | 1.925 | 45.107 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4531_12_1_03112020_80.tiff | ./EL/4531_12_1_03112020_20.tiff | ./IV/4531_12_1_03102020.csv | 0 | 0 | 1 | ./RefIV/4531_12_1_03102020.csv | 8.862 | 8.862 | 2020-10-03 | 14:44 | 0.99502 | 1.0138
378 | 4515 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.623 | 47.44 | 9.209 | 0.95698 | 39.05 | 0.82315 | 359.7 | 78.8 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 14:02 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.498 | 12.8 | 1.925 | 44.957 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4515_12_1_03112020_80.tiff | ./EL/4515_12_1_03112020_20.tiff | ./IV/4515_12_1_03102020.csv | 0 | 0 | 1 | ./RefIV/4515_12_1_03102020.csv | 8.862 | 8.862 | 2020-10-03 | 14:02 | 0.99526 | 1.0119
379 | 4523 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.602 | 47.33 | 9.179 | 0.95595 | 38.8 | 0.81978 | 356.1 | 78.4 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 14:25 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.498 | 12.8 | 1.925 | 44.882 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4523_12_1_03112020_80.tiff | ./EL/4523_12_1_03112020_20.tiff | ./IV/4523_12_1_03102020.csv | 0 | 0 | 1 | ./RefIV/4523_12_1_03102020.csv | 8.862 | 8.862 | 2020-10-03 | 14:25 | 0.99418 | 1.0078
380 | 4552 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.547 | 47.41 | 9.137 | 0.95705 | 39.1 | 0.82472 | 357.2 | 78.9 | 25 | back of panel |  | SPIRE | 4600SLP | 3/17/2020 | 9:27 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.461 | 12.8 | 1.925 | 44.882 | 51.2 |  |  |  |  | 2.69 | 3/23/2020 |  | 3/23/2020 |  | PSEL | ./EL/4552_12_1_03232020_80.tiff | ./EL/4552_12_1_03232020_20.tiff | ./IV/4552_12_1_03172020.csv | 0 | 0 | 1 | ./RefIV/4552_12_1_03172020.csv | 8.862 | 8.862 | 3/17/2020 | 9:27 | 0.99534 | 1.0139
381 | 4543 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.583 | 47.46 | 9.161 | 0.95596 | 39.18 | 0.82554 | 358.9 | 78.9 | 25 | back of panel |  | SPIRE | 4600SLP | 3/17/2020 | 9:08 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.348 | 12.8 | 1.925 | 44.882 | 51.21 |  |  |  |  | 2.69 | 3/23/2020 |  | 3/23/2020 |  | PSEL | ./EL/4543_12_1_03232020_80.tiff | ./EL/4543_12_1_03232020_20.tiff | ./IV/4543_12_1_03172020.csv | 0 | 0 | 1 | ./RefIV/4543_12_1_03172020.csv | 8.862 | 8.862 | 3/17/2020 | 9:08 | 0.9942 | 1.0149
382 | 4544 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.556 | 47.39 | 9.143 | 0.95678 | 39.09 | 0.82486 | 357.4 | 78.9 | 24.9 | back of panel |  | SPIRE | 4600SLP | 3/17/2020 | 9:11 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.348 | 12.8 | 1.925 | 44.882 | 51.2 |  |  |  |  | 2.69 | 3/23/2020 |  | 3/23/2020 |  | PSEL | ./EL/4544_12_1_03232020_80.tiff | ./EL/4544_12_1_03232020_20.tiff | ./IV/4544_12_1_03172020.csv | 0 | 0 | 1 | ./RefIV/4544_12_1_03172020.csv | 8.862 | 8.862 | 3/17/2020 | 9:11 | 0.99505 | 1.014
383 | 4545 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.556 | 47.37 | 9.158 | 0.95835 | 39.06 | 0.82457 | 357.7 | 79 | 25 | back of panel |  | SPIRE | 4600SLP | 3/17/2020 | 9:12 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.348 | 12.8 | 1.925 | 44.882 | 51.2 |  |  |  |  | 2.69 | 3/23/2020 |  | 3/23/2020 |  | PSEL | ./EL/4545_12_1_03232020_80.tiff | ./EL/4545_12_1_03232020_20.tiff | ./IV/4545_12_1_03172020.csv | 0 | 0 | 1 | ./RefIV/4545_12_1_03172020.csv | 8.862 | 8.862 | 3/17/2020 | 9:12 | 0.99668 | 1.0137
384 | 4534 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.615 | 47.45 | 9.188 | 0.95559 | 39.01 | 0.82213 | 358.5 | 78.6 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 14:55 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.686 | 12.8 | 1.925 | 45.032 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4534_12_1_03112020_80.tiff | ./EL/4534_12_1_03112020_20.tiff | ./IV/4534_12_1_03102020.csv | 0 | 1 | 2 | ./RefIV/4534_12_1_03102020.csv | 8.862 | 8.862 | 2020-10-03 | 14:55 | 0.99381 | 1.0107
385 | 4534 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 329 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.536 | 47.13 | 9.12 | 0.95638 | 38.61 | 0.81922 | 352.1 | 78.3 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-02-02 | 10:03 | PSEL | FLI Proline |  |  |  |  | 7.638 | 48.447 | 12.8 | 1.91 | 43.944 | 51.2 |  |  |  |  | 2.76 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/4534_12_1_02082021_80.tiff | ./EL/4534_12_1_02082021_20.tiff | ./IV/4534_12_1_02022021.csv | 0 | 0 | 2 | ./RefIV/4534_12_1_02022021.csv | 8.862 | 8.862 | 2020-10-03 | 14:55 | 0.99463 | 1.0071
386 | 4520 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.619 | 47.38 | 9.211 | 0.95758 | 39 | 0.82313 | 359.2 | 78.8 | 24.6 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 14:12 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.611 | 12.8 | 1.925 | 45.995 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4520_12_1_03112020_80.tiff | ./EL/4520_12_1_03112020_20.tiff | ./IV/4520_12_1_03102020.csv | 0 | 0 | 1 | ./RefIV/4520_12_1_03102020.csv | 8.862 | 8.862 | 2020-10-03 | 14:12 | 0.99589 | 1.0119
387 | 4537 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.632 | 47.33 | 9.203 | 0.95546 | 38.98 | 0.82358 | 358.7 | 78.7 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 15:02 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.536 | 12.8 | 1.92 | 44.957 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4537_12_1_03112020_80.tiff | ./EL/4537_12_1_03112020_20.tiff | ./IV/4537_12_1_03102020.csv | 0 | 0 | 1 | ./RefIV/4537_12_1_03102020.csv | 8.862 | 8.862 | 2020-10-03 | 15:02 | 0.99368 | 1.0124
388 | 4553 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.563 | 47.37 | 9.141 | 0.95587 | 39.01 | 0.82352 | 356.6 | 78.7 | 25 | back of panel |  | SPIRE | 4600SLP | 3/17/2020 | 9:29 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.423 | 12.8 | 1.92 | 44.807 | 51.2 |  |  |  |  | 2.69 | 3/23/2020 |  | 3/23/2020 |  | PSEL | ./EL/4553_12_1_03232020_80.tiff | ./EL/4553_12_1_03232020_20.tiff | ./IV/4553_12_1_03172020.csv | 0 | 0 | 1 | ./RefIV/4553_12_1_03172020.csv | 8.862 | 8.862 | 3/17/2020 | 9:29 | 0.99411 | 1.0124
389 | 4532 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.618 | 47.47 | 9.206 | 0.95716 | 39.06 | 0.82284 | 359.6 | 78.8 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 14:46 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.686 | 12.8 | 1.92 | 45.107 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4532_12_1_03112020_80.tiff | ./EL/4532_12_1_03112020_20.tiff | ./IV/4532_12_1_03102020.csv | 0 | 0 | 1 | ./RefIV/4532_12_1_03102020.csv | 8.862 | 8.862 | 2020-10-03 | 14:46 | 0.99545 | 1.0115
390 | 4528 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.61 | 47.4 | 9.2 | 0.95734 | 38.95 | 0.82173 | 358.3 | 78.7 | 25.3 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 14:38 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.498 | 12.8 | 1.92 | 44.957 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4528_12_1_03112020_80.tiff | ./EL/4528_12_1_03112020_20.tiff | ./IV/4528_12_1_03102020.csv | 0 | 0 | 1 | ./RefIV/4528_12_1_03102020.csv | 8.862 | 8.862 | 2020-10-03 | 14:38 | 0.99563 | 1.0102
391 | 4526 |  | 12 | 1 |  | 19949.9 |  | mono-Si module |  |  | OE 0 days | 9.62 | 47.87 | 9.25 | 0.96154 | 38.94 | 0.81345 | 360 | 9.608 | 47.37 | 9.196 | 0.95712 | 38.93 | 0.82183 | 358 | 78.7 | 25.3 | back of panel |  | SPIRE | 4600SLP | 2020-10-03 | 14:34 | PSEL | FLI Proline |  |  |  |  | 7.698 | 49.386 | 12.8 | 1.925 | 44.844 | 51.2 |  |  |  |  | 2.69 | 2020-11-03 |  | 2020-11-03 |  | PSEL | ./EL/4526_12_1_03112020_80.tiff | ./EL/4526_12_1_03112020_20.tiff | ./IV/4526_12_1_03102020.csv | 0 | 0 | 1 | ./RefIV/4526_12_1_03102020.csv | 8.862 | 8.862 | 2020-10-03 | 14:34 | 0.9954 | 1.0103
392 | 3458 |  | 38 | 4 |  | 16335 |  | multi-Si module |  |  | OE 1685 days | 8.67 | 37.9 | 8.2 | 0.94579 | 31.7 | 0.83641 | 260 | 9.058 | 37.78 | 8.6 | 0.94944 | 30.75 | 0.81392 | 264.5 | 77.3 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 9:24 | PSEL | FLI Proline |  |  |  |  | 7.258 | 38.839 | 51.2 | 1.815 | 34.974 | 204.6 |  |  |  |  | 2.36 | 1/29/2021 |  | 1/29/2021 |  | PSEL | ./EL/3458_38_4_01292021_80.tiff | ./EL/3458_38_4_01292021_20.tiff | ./IV/3458_38_4_02092021.csv | 0 | 0 | 1 | ./RefIV/3458_38_4_02092021.csv | 8.862 |  | 6/30/2016 | 15:52 | 1.0039 | 0.97311
393 | 3416 |  | 38 | 4 |  | 16335 |  | multi-Si module |  |  | OE 1686 days | 8.67 | 37.9 | 8.2 | 0.94579 | 31.7 | 0.83641 | 260 | 9.014 | 37.75 | 8.55 | 0.94852 | 30.73 | 0.81404 | 262.7 | 77.2 | 25 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 9:21 | PSEL | FLI Proline |  |  |  |  | 7.3 | 39 | 51.2 | 1.8 | 34.8 | 204.6 |  |  |  |  | 2.36 | 1/29/2021 |  | 1/29/2021 |  | PSEL | ./EL/3416_38_4_01292021_80.tiff | ./EL/3416_38_4_01292021_20.tiff | ./IV/3416_38_4_02092021.csv | 0 | 0 | 1 | ./RefIV/3416_38_4_02092021.csv | 8.862 |  | 6/29/2016 | 17:50 | 1.0029 | 0.97325
394 | 3420 |  | 38 | 4 |  | 16335 |  | multi-Si module |  |  | OE 1686 days | 8.67 | 37.9 | 8.2 | 0.94579 | 31.7 | 0.83641 | 260 | 9.05 | 37.62 | 8.549 | 0.94464 | 30.59 | 0.81313 | 261.6 | 76.8 | 24.8 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 9:15 | PSEL | FLI Proline |  |  |  |  | 7.3 | 39 | 51.2 | 1.8 | 34.6 | 204.6 |  |  |  |  | 2.36 | 1/29/2021 |  | 1/29/2021 |  | PSEL | ./EL/3420_38_4_01292021_80.tiff | ./EL/3420_38_4_01292021_20.tiff | ./IV/3420_38_4_02092021.csv | 0 | 0 | 1 | ./RefIV/3420_38_4_02092021.csv | 8.862 |  | 6/29/2016 | 18:38 | 0.99878 | 0.97217
395 | 3427 |  | 38 | 4 |  | 16335 |  | multi-Si module |  |  | OE 1686 days | 8.67 | 37.9 | 8.2 | 0.94579 | 31.7 | 0.83641 | 260 | 9.043 | 37.76 | 8.567 | 0.94736 | 30.6 | 0.81038 | 262.1 | 76.8 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 9:16 | PSEL | FLI Proline |  |  |  |  | 7.3 | 39.1 | 51.2 | 1.8 | 35.2 | 204.6 |  |  |  |  | 2.36 | 1/29/2021 |  | 1/29/2021 |  | PSEL | ./EL/3427_38_4_01292021_80.tiff | ./EL/3427_38_4_01292021_20.tiff | ./IV/3427_38_4_02092021.csv | 0 | 0 | 1 | ./RefIV/3427_38_4_02092021.csv | 8.862 |  | 6/29/2016 | 18:09 | 1.0017 | 0.96888
396 | 3453 |  | 38 | 4 |  | 16335 |  | multi-Si module |  |  | OE 1685 days | 8.67 | 37.9 | 8.2 | 0.94579 | 31.7 | 0.83641 | 260 | 9.065 | 37.77 | 8.576 | 0.94606 | 30.78 | 0.81493 | 264 | 77.1 | 24.8 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 9:19 | PSEL | FLI Proline |  |  |  |  | 7.3 | 39.1 | 51.2 | 1.8 | 35.1 | 204.6 |  |  |  |  | 2.36 | 1/29/2021 |  | 1/29/2021 |  | PSEL | ./EL/3453_38_4_01292021_80.tiff | ./EL/3453_38_4_01292021_20.tiff | ./IV/3453_38_4_02092021.csv | 0 | 0 | 1 | ./RefIV/3453_38_4_02092021.csv | 8.862 |  | 6/30/2016 | 16:25 | 1.0003 | 0.97432
397 | 3471 |  | 38 | 4 |  | 16335 |  | multi-Si module |  |  | OE 1029 days | 8.67 | 37.9 | 8.2 | 0.94579 | 31.7 | 0.83641 | 260 | 9.078 | 37.86 | 8.622 | 0.94977 | 30.78 | 0.813 | 265.4 | 77.2 | 24.6 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 9:13 | PSEL | FLI Proline |  |  |  |  | 7.3 | 39.1 | 51.2 | 1.8 | 35.2 | 204.6 |  |  |  |  | 2.36 | 1/29/2021 |  | 1/29/2021 |  | PSEL | ./EL/3471_38_4_01292021_80.tiff | ./EL/3471_38_4_01292021_20.tiff | ./IV/3471_38_4_02092021.csv | 0 | 0 | 1 | ./RefIV/3471_38_4_02092021.csv | 8.862 | 8.862 | 4/17/2018 | 9:13 | 1.0042 | 0.972
398 | 3413 |  | 38 | 4 |  | 16335 |  | multi-Si module |  |  | OE 1686 days | 8.67 | 37.9 | 8.2 | 0.94579 | 31.7 | 0.83641 | 260 | 9.073 | 37.67 | 8.569 | 0.94445 | 30.7 | 0.81497 | 263.1 | 77 | 25 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 9:20 | PSEL | FLI Proline |  |  |  |  | 7.3 | 39 | 51.2 | 1.8 | 34.8 | 204.6 |  |  |  |  | 2.36 | 1/29/2021 |  | 1/29/2021 |  | PSEL | ./EL/3413_38_4_01292021_80.tiff | ./EL/3413_38_4_01292021_20.tiff | ./IV/3413_38_4_02092021.csv | 0 | 0 | 1 | ./RefIV/3413_38_4_02092021.csv | 8.862 |  | 6/29/2016 | 17:59 | 0.99858 | 0.97437
399 | 3452 |  | 38 | 4 |  | 16335 |  | multi-Si module |  |  | OE 1685 days | 8.67 | 37.9 | 8.2 | 0.94579 | 31.7 | 0.83641 | 260 | 9.105 | 37.79 | 8.613 | 0.94596 | 30.74 | 0.81344 | 264.7 | 76.9 | 25 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 9:29 | PSEL | FLI Proline |  |  |  |  | 7.263 | 38.802 | 51.2 | 1.815 | 34.861 | 204.6 |  |  |  |  | 2.36 | 1/29/2021 |  | 1/29/2021 |  | PSEL | ./EL/3452_38_4_01292021_80.tiff | ./EL/3452_38_4_01292021_20.tiff | ./IV/3452_38_4_02092021.csv | 0 | 0 | 1 | ./RefIV/3452_38_4_02092021.csv | 8.862 |  | 6/30/2016 | 16:31 | 1.0002 | 0.97254
400 | 3465 |  | 38 | 4 |  | 16335 |  | multi-Si module |  |  | OE 1685 days | 8.67 | 37.9 | 8.2 | 0.94579 | 31.7 | 0.83641 | 260 | 9.03 | 37.87 | 8.546 | 0.9464 | 30.65 | 0.80935 | 261.9 | 76.6 | 24.6 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 9:11 | PSEL | FLI Proline |  |  |  |  | 7.3 | 39.1 | 51.2 | 1.8 | 35.1 | 204.6 |  |  |  |  | 2.36 | 1/29/2021 |  | 1/29/2021 |  | PSEL | ./EL/3465_38_4_01292021_80.tiff | ./EL/3465_38_4_01292021_20.tiff | ./IV/3465_38_4_02092021.csv | 0 | 0 | 1 | ./RefIV/3465_38_4_02092021.csv | 8.862 |  | 6/30/2016 | 15:19 | 1.0006 | 0.96764
401 | 3417 |  | 38 | 4 |  | 16335 |  | multi-Si module |  |  | OE 1686 days | 8.67 | 37.9 | 8.2 | 0.94579 | 31.7 | 0.83641 | 260 | 9.086 | 37.67 | 8.576 | 0.94387 | 30.63 | 0.81311 | 262.6 | 76.7 | 25 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 9:22 | PSEL | FLI Proline |  |  |  |  | 7.258 | 39.14 | 51.2 | 1.815 | 34.936 | 204.6 |  |  |  |  | 2.36 | 1/29/2021 |  | 1/29/2021 |  | PSEL | ./EL/3417_38_4_01292021_80.tiff | ./EL/3417_38_4_01292021_20.tiff | ./IV/3417_38_4_02092021.csv | 0 | 0 | 1 | ./RefIV/3417_38_4_02092021.csv | 8.862 |  | 6/29/2016 | 18:46 | 0.99797 | 0.97215
402 | 3459 |  | 38 | 4 |  | 16335 |  | multi-Si module |  |  | OE 1685 days | 8.67 | 37.9 | 8.2 | 0.94579 | 31.7 | 0.83641 | 260 | 9.08 | 37.92 | 8.605 | 0.94769 | 30.85 | 0.81355 | 265.5 | 77.1 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 9:28 | PSEL | FLI Proline |  |  |  |  | 7.258 | 38.727 | 51.2 | 1.815 | 34.824 | 204.6 |  |  |  |  | 2.36 | 1/29/2021 |  | 1/29/2021 |  | PSEL | ./EL/3459_38_4_01292021_80.tiff | ./EL/3459_38_4_01292021_20.tiff | ./IV/3459_38_4_02092021.csv | 0 | 0 | 1 | ./RefIV/3459_38_4_02092021.csv | 8.862 |  | 6/30/2016 | 15:48 | 1.002 | 0.97267
403 | 3456 |  | 38 | 4 |  | 16335 |  | multi-Si module |  |  | OE 1685 days | 8.67 | 37.9 | 8.2 | 0.94579 | 31.7 | 0.83641 | 260 | 9.045 | 37.73 | 8.571 | 0.9476 | 30.71 | 0.81394 | 263.3 | 77.1 | 25 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 9:23 | PSEL | FLI Proline |  |  |  |  | 7.258 | 39.29 | 51.2 | 1.815 | 34.899 | 204.6 |  |  |  |  | 2.36 | 1/29/2021 |  | 1/29/2021 |  | PSEL | ./EL/3456_38_4_01292021_80.tiff | ./EL/3456_38_4_01292021_20.tiff | ./IV/3456_38_4_02092021.csv | 0 | 0 | 1 | ./RefIV/3456_38_4_02092021.csv | 8.862 |  | 6/30/2016 | 16:17 | 1.0019 | 0.97313
404 | 3457 |  | 38 | 4 |  | 16335 |  | multi-Si module |  |  | OE 1685 days | 8.67 | 37.9 | 8.2 | 0.94579 | 31.7 | 0.83641 | 260 | 9.108 | 37.77 | 8.594 | 0.94357 | 30.7 | 0.81281 | 263.9 | 76.7 | 25 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 9:18 | PSEL | FLI Proline |  |  |  |  | 7.3 | 38.9 | 51.2 | 1.8 | 35.1 | 204.6 |  |  |  |  | 2.36 | 1/29/2021 |  | 1/29/2021 |  | PSEL | ./EL/3457_38_4_01292021_80.tiff | ./EL/3457_38_4_01292021_20.tiff | ./IV/3457_38_4_02092021.csv | 0 | 0 | 1 | ./RefIV/3457_38_4_02092021.csv | 8.862 |  | 6/30/2016 | 16:09 | 0.99765 | 0.97179
405 | 3463 |  | 38 | 4 |  | 16335 |  | multi-Si module |  |  | OE 1685 days | 8.67 | 37.9 | 8.2 | 0.94579 | 31.7 | 0.83641 | 260 | 9.051 | 37.81 | 8.585 | 0.94851 | 30.8 | 0.8146 | 264.4 | 77.3 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 9:17 | PSEL | FLI Proline |  |  |  |  | 7.3 | 39.1 | 51.2 | 1.8 | 35.1 | 204.6 |  |  |  |  | 2.36 | 1/29/2021 |  | 1/29/2021 |  | PSEL | ./EL/3463_38_4_01292021_80.tiff | ./EL/3463_38_4_01292021_20.tiff | ./IV/3463_38_4_02092021.csv | 0 | 0 | 1 | ./RefIV/3463_38_4_02092021.csv | 8.862 |  | 6/30/2016 | 15:32 | 1.0029 | 0.97392
406 | 3436 |  | 38 | 4 |  | 16335 |  | multi-Si module |  |  | OE 1686 days | 8.67 | 37.9 | 8.2 | 0.94579 | 31.7 | 0.83641 | 260 | 9.043 | 37.73 | 8.562 | 0.94681 | 30.73 | 0.81447 | 263.1 | 77.1 | 25 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 9:29 | PSEL | FLI Proline |  |  |  |  | 7.263 | 38.838 | 51.2 | 1.815 | 34.748 | 204.6 |  |  |  |  | 2.36 | 1/29/2021 |  | 1/29/2021 |  | PSEL | ./EL/3436_38_4_01292021_80.tiff | ./EL/3436_38_4_01292021_20.tiff | ./IV/3436_38_4_02092021.csv | 0 | 0 | 1 | ./RefIV/3436_38_4_02092021.csv | 8.862 |  | 6/29/2016 | 17:11 | 1.0011 | 0.97377
407 | 3441 |  | 38 | 4 |  | 16335 |  | multi-Si module |  |  | OE 1686 days | 8.67 | 37.9 | 8.2 | 0.94579 | 31.7 | 0.83641 | 260 | 9.043 | 37.71 | 8.562 | 0.94681 | 30.71 | 0.81437 | 262.9 | 77.1 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-09-02 | 9:30 | PSEL | FLI Proline |  |  |  |  | 7.258 | 38.727 | 51.2 | 1.815 | 34.673 | 204.6 |  |  |  |  | 2.36 | 1/29/2021 |  | 1/29/2021 |  | PSEL | ./EL/3441_38_4_01292021_80.tiff | ./EL/3441_38_4_01292021_20.tiff | ./IV/3441_38_4_02092021.csv | 0 | 0 | 1 | ./RefIV/3441_38_4_02092021.csv | 8.862 |  | 6/29/2016 | 19:11 | 1.0011 | 0.97365
408 | 3865 |  | 17 | 1 |  | 17123 |  | mono-Si module |  |  | OE 1120 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.11 | 40.15 | 9.625 | 0.95203 | 32.85 | 0.81818 | 316.2 | 77.9 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-10-02 | 13:17 | PSEL | FLI Proline |  |  |  |  | 8.1 | 41.5 | 6.4 | 2 | 37.8 | 25.6 |  |  |  |  | 2.36 | 2/22/2021 |  | 2/22/2021 |  | PSEL | ./EL/3865_17_1_02222021_80.tiff | ./EL/3865_17_1_02222021_20.tiff | ./IV/3865_17_1_02102021.csv | 0 | 1 | 2 | ./RefIV/3865_17_1_02102021.csv | 8.862 | 9.248 | 1/17/2018 | 12:20 | 1.0084 | 1.0025
409 | 3865 |  | 17 | 1 |  | 17123 |  | mono-Si module |  |  | OE 734 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.12 | 40.22 | 9.633 | 0.95188 | 32.97 | 0.81974 | 317.6 | 78.1 | 24.8 | back of panel |  | SPIRE | 4600SLP | 1/21/2020 | 11:54 | PSEL | FLI Proline |  |  |  |  | 8.092 | 41.729 | 6.4 | 2.025 | 38.014 | 25.6 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/3865_17_1_01302020_80.tiff | ./EL/3865_17_1_01302020_20.tiff | ./IV/3865_17_1_01212020.csv | 0 | 0 | 2 | ./RefIV/3865_17_1_01212020.csv | 8.862 | 9.248 | 1/17/2018 | 12:20 | 1.0083 | 1.0044
410 | 3873 |  | 17 | 1 |  | 17123 |  | mono-Si module |  |  | OE 1120 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.1 | 40.09 | 9.64 | 0.95446 | 32.74 | 0.81666 | 315.6 | 77.9 | 25.3 | back of panel |  | SPIRE | 4600SLP | 2021-10-02 | 13:24 | PSEL | FLI Proline |  |  |  |  | 8.1 | 41.5 | 6.4 | 2 | 37.7 | 25.6 |  |  |  |  | 2.36 | 2/22/2021 |  | 2/22/2021 |  | PSEL | ./EL/3873_17_1_02222021_80.tiff | ./EL/3873_17_1_02222021_20.tiff | ./IV/3873_17_1_02102021.csv | 0 | 0 | 1 | ./RefIV/3873_17_1_02102021.csv | 8.862 | 9.248 | 1/17/2018 | 15:29 | 1.011 | 1.0006
411 | 3858 |  | 17 | 1 |  | 17123 |  | mono-Si module |  |  | OE 1120 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.15 | 40.04 | 9.63 | 0.94877 | 32.67 | 0.81593 | 314.6 | 77.4 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-10-02 | 13:20 | PSEL | FLI Proline |  |  |  |  | 8.1 | 41.4 | 6.4 | 2 | 37.7 | 25.6 |  |  |  |  | 2.36 | 2/22/2021 |  | 2/22/2021 |  | PSEL | ./EL/3858_17_1_02222021_80.tiff | ./EL/3858_17_1_02222021_20.tiff | ./IV/3858_17_1_02102021.csv | 0 | 1 | 2 | ./RefIV/3858_17_1_02102021.csv | 8.862 | 9.248 | 1/17/2018 | 9:23 | 1.005 | 0.9997
412 | 3858 |  | 17 | 1 |  | 17123 |  | mono-Si module |  |  | OE 734 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.16 | 40.11 | 9.646 | 0.94941 | 32.77 | 0.817 | 316.1 | 77.6 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/21/2020 | 11:34 | PSEL | FLI Proline |  |  |  |  | 8.093 | 41.692 | 6.4 | 2.02 | 37.939 | 35.6 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/3858_17_1_01302020_80.tiff | ./EL/3858_17_1_01302020_20.tiff | ./IV/3858_17_1_01212020.csv | 0 | 0 | 2 | ./RefIV/3858_17_1_01212020.csv | 8.862 | 9.248 | 1/17/2018 | 9:23 | 1.0057 | 1.001
413 | 3874 |  | 17 | 1 |  | 17123 |  | mono-Si module |  |  | OE 1120 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.09 | 40.14 | 9.616 | 0.95302 | 32.8 | 0.81714 | 315.4 | 77.9 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-10-02 | 13:25 | PSEL | FLI Proline |  |  |  |  | 8.1 | 41.6 | 6.4 | 2 | 37.9 | 25.6 |  |  |  |  | 2.36 | 2/22/2021 |  | 2/22/2021 |  | PSEL | ./EL/3874_17_1_02222021_80.tiff | ./EL/3874_17_1_02222021_20.tiff | ./IV/3874_17_1_02102021.csv | 0 | 1 | 2 | ./RefIV/3874_17_1_02102021.csv | 8.862 | 9.248 | 1/17/2018 | 15:38 | 1.0095 | 1.0012
414 | 3874 |  | 17 | 1 |  | 17123 |  | mono-Si module |  |  | OE 734 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.1 | 40.2 | 9.627 | 0.95317 | 32.92 | 0.81891 | 317 | 78.1 | 24.8 | back of panel |  | SPIRE | 4600SLP | 1/21/2020 | 11:23 | PSEL | FLI Proline |  |  |  |  | 8.092 | 41.729 | 6.4 | 2.02 | 38.014 | 25.6 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/3874_17_1_01302020_80.tiff | ./EL/3874_17_1_01302020_20.tiff | ./IV/3874_17_1_01212020.csv | 0 | 0 | 2 | ./RefIV/3874_17_1_01212020.csv | 8.862 | 9.248 | 1/17/2018 | 15:38 | 1.0096 | 1.0033
415 | 3870 |  | 17 | 1 |  | 17123 |  | mono-Si module |  |  | OE 1120 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.1 | 40.09 | 9.625 | 0.95297 | 32.74 | 0.81666 | 315.1 | 77.9 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-10-02 | 13:23 | PSEL | FLI Proline |  |  |  |  | 8.1 | 41.4 | 6.4 | 2 | 37.7 | 25.6 |  |  |  |  | 2.36 | 2/22/2021 |  | 2/22/2021 |  | PSEL | ./EL/3870_17_1_02222021_80.tiff | ./EL/3870_17_1_02222021_20.tiff | ./IV/3870_17_1_02102021.csv | 0 | 1 | 2 | ./RefIV/3870_17_1_02102021.csv | 8.862 | 9.248 | 1/17/2018 | 13:31 | 1.0094 | 1.0006
416 | 3870 |  | 17 | 1 |  | 17123 |  | mono-Si module |  |  | OE 734 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.1 | 40.15 | 9.64 | 0.95446 | 32.88 | 0.81893 | 317 | 78.2 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/21/2020 | 11:27 | PSEL | FLI Proline |  |  |  |  | 8.092 | 41.729 | 6.4 | 2.025 | 38.014 | 25.6 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/3870_17_1_01302020_80.tiff | ./EL/3870_17_1_01302020_20.tiff | ./IV/3870_17_1_01212020.csv | 0 | 0 | 2 | ./RefIV/3870_17_1_01212020.csv | 8.862 | 9.248 | 1/17/2018 | 13:31 | 1.011 | 1.0034
417 | 3868 |  | 17 | 1 |  | 17123 |  | mono-Si module |  |  | OE 1120 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.16 | 40.17 | 9.666 | 0.95138 | 32.81 | 0.81678 | 317.1 | 77.7 | 25 | back of panel |  | SPIRE | 4600SLP | 2021-10-02 | 13:10 | PSEL | FLI Proline |  |  |  |  | 8.1 | 41.3 | 6.4 | 2 | 37.6 | 25.6 |  |  |  |  | 2.36 | 2/22/2021 |  | 2/22/2021 |  | PSEL | ./EL/3868_17_1_02222021_80.tiff | ./EL/3868_17_1_02222021_20.tiff | ./IV/3868_17_1_02102021.csv | 0 | 1 | 2 | ./RefIV/3868_17_1_02102021.csv | 8.862 | 9.248 | 1/17/2018 | 13:00 | 1.0077 | 1.0007
418 | 3868 |  | 17 | 1 |  | 17123 |  | mono-Si module |  |  | OE 734 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.08 | 40.36 | 9.618 | 0.95417 | 33.04 | 0.81863 | 317.7 | 78.1 | 24.8 | back of panel |  | SPIRE | 4600SLP | 1/21/2020 | 11:15 | PSEL | FLI Proline |  |  |  |  | 8.097 | 41.692 | 6.4 | 2.02 | 37.713 | 19.2 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/3868_17_1_01302020_80.tiff | ./EL/3868_17_1_01302020_20.tiff | ./IV/3868_17_1_01212020.csv | 0 | 0 | 2 | ./RefIV/3868_17_1_01212020.csv | 8.862 | 9.248 | 1/17/2018 | 13:00 | 1.0107 | 1.003
419 | 3866 |  | 17 | 1 |  | 17123 |  | mono-Si module |  |  | OE 1120 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.09 | 40.1 | 9.631 | 0.95451 | 32.77 | 0.81721 | 315.6 | 78 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-10-02 | 13:16 | PSEL | FLI Proline |  |  |  |  | 8.1 | 41.4 | 6.4 | 2 | 37.7 | 25.6 |  |  |  |  | 2.36 | 2/22/2021 |  | 2/22/2021 |  | PSEL | ./EL/3866_17_1_02222021_80.tiff | ./EL/3866_17_1_02222021_20.tiff | ./IV/3866_17_1_02102021.csv | 0 | 1 | 2 | ./RefIV/3866_17_1_02102021.csv | 8.862 | 9.248 | 1/17/2018 | 12:27 | 1.0111 | 1.0013
420 | 3866 |  | 17 | 1 |  | 17123 |  | mono-Si module |  |  | OE 734 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.1 | 40.15 | 9.641 | 0.95455 | 32.88 | 0.81893 | 317 | 78.1 | 24.8 | back of panel |  | SPIRE | 4600SLP | 1/21/2020 | 11:40 | PSEL | FLI Proline |  |  |  |  | 8.092 | 41.729 | 6.4 | 2.02 | 38.014 | 25.6 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/3866_17_1_01302020_80.tiff | ./EL/3866_17_1_01302020_20.tiff | ./IV/3866_17_1_01212020.csv | 0 | 0 | 2 | ./RefIV/3866_17_1_01212020.csv | 8.862 | 9.248 | 1/17/2018 | 12:27 | 1.0111 | 1.0034
421 | 4061 |  | 17 | 1 |  | 17123 |  | mono-Si module |  |  | OE 940 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.15 | 40.13 | 9.664 | 0.95212 | 32.81 | 0.81759 | 317.1 | 77.8 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-10-02 | 13:15 | PSEL | FLI Proline |  |  |  |  | 8.1 | 41.5 | 6.4 | 2 | 37.8 | 25.6 |  |  |  |  | 2.36 | 2/22/2021 |  | 2/22/2021 |  | PSEL | ./EL/4061_17_1_02222021_80.tiff | ./EL/4061_17_1_02222021_20.tiff | ./IV/4061_17_1_02102021.csv | 0 | 0 | 1 | ./RefIV/4061_17_1_02102021.csv | 8.862 | 8.862 | 7/16/2018 | 15:34 | 1.0085 | 1.0017
422 | 4050 |  | 17 | 1 |  | 17123 |  | mono-Si module |  |  | OE 940 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.14 | 40.12 | 9.653 | 0.95197 | 32.86 | 0.81904 | 317.2 | 78 | 25.3 | back of panel |  | SPIRE | 4600SLP | 2021-10-02 | 13:13 | PSEL | FLI Proline |  |  |  |  | 8.1 | 41.4 | 6.4 | 2 | 37.7 | 25.6 |  |  |  |  | 2.36 | 2/22/2021 |  | 2/22/2021 |  | PSEL | ./EL/4050_17_1_02222021_80.tiff | ./EL/4050_17_1_02222021_20.tiff | ./IV/4050_17_1_02102021.csv | 0 | 0 | 1 | ./RefIV/4050_17_1_02102021.csv | 8.862 | 8.862 | 7/16/2018 | 14:26 | 1.0084 | 1.0035
423 | 3857 |  | 17 | 1 |  | 17123 |  | mono-Si module |  |  | OE 1120 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.13 | 40.12 | 9.637 | 0.95133 | 32.79 | 0.8173 | 316 | 77.7 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-10-02 | 13:20 | PSEL | FLI Proline |  |  |  |  | 8.1 | 41.5 | 6.4 | 2 | 37.8 | 25.6 |  |  |  |  | 2.36 | 2/22/2021 |  | 2/22/2021 |  | PSEL | ./EL/3857_17_1_02222021_80.tiff | ./EL/3857_17_1_02222021_20.tiff | ./IV/3857_17_1_02102021.csv | 0 | 1 | 2 | ./RefIV/3857_17_1_02102021.csv | 8.862 | 9.248 | 1/17/2018 | 9:16 | 1.0077 | 1.0014
424 | 3857 |  | 17 | 1 |  | 17123 |  | mono-Si module |  |  | OE 734 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.13 | 40.19 | 9.648 | 0.95242 | 32.92 | 0.81911 | 317.6 | 78 | 24.8 | back of panel |  | SPIRE | 4600SLP | 1/21/2020 | 11:32 | PSEL | FLI Proline |  |  |  |  | 8.097 | 41.729 | 6.4 | 2.02 | 38.014 | 19.2 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/3857_17_1_01302020_80.tiff | ./EL/3857_17_1_01302020_20.tiff | ./IV/3857_17_1_01212020.csv | 0 | 0 | 2 | ./RefIV/3857_17_1_01212020.csv | 8.862 | 9.248 | 1/17/2018 | 9:16 | 1.0089 | 1.0036
425 | 3880 |  | 17 | 1 |  | 17123 |  | mono-Si module |  |  | OE 1120 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.13 | 40.14 | 9.626 | 0.95025 | 32.79 | 0.81689 | 315.7 | 77.7 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-10-02 | 13:21 | PSEL | FLI Proline |  |  |  |  | 8.1 | 41.5 | 6.4 | 2 | 37.8 | 25.6 |  |  |  |  | 2.36 | 2/22/2021 |  | 2/22/2021 |  | PSEL | ./EL/3880_17_1_02222021_80.tiff | ./EL/3880_17_1_02222021_20.tiff | ./IV/3880_17_1_02102021.csv | 0 | 1 | 2 | ./RefIV/3880_17_1_02102021.csv | 8.862 | 9.248 | 1/17/2018 | 16:19 | 1.0066 | 1.0009
426 | 3880 |  | 17 | 1 |  | 17123 |  | mono-Si module |  |  | OE 734 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.13 | 40.21 | 9.637 | 0.95133 | 32.92 | 0.8187 | 317.2 | 77.9 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/21/2020 | 11:30 | PSEL | FLI Proline |  |  |  |  | 8.097 | 41.767 | 6.4 | 1.201 | 36.963 | 25.6 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/3880_17_1_01302020_80.tiff | ./EL/3880_17_1_01302020_20.tiff | ./IV/3880_17_1_01212020.csv | 0 | 0 | 2 | ./RefIV/3880_17_1_01212020.csv | 8.862 | 9.248 | 1/17/2018 | 16:19 | 1.0077 | 1.0031
427 | 3878 |  | 17 | 1 |  | 17123 |  | mono-Si module |  |  | OE 1120 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.09 | 40.09 | 9.633 | 0.95471 | 32.82 | 0.81866 | 316.2 | 78.2 | 25.4 | back of panel |  | SPIRE | 4600SLP | 2021-10-02 | 13:27 | PSEL | FLI Proline |  |  |  |  | 8.1 | 41.4 | 6.4 | 2 | 37.8 | 25.6 |  |  |  |  | 2.36 | 2/22/2021 |  | 2/22/2021 |  | PSEL | ./EL/3878_17_1_02222021_80.tiff | ./EL/3878_17_1_02222021_20.tiff | ./IV/3878_17_1_02102021.csv | 0 | 0 | 1 | ./RefIV/3878_17_1_02102021.csv | 8.862 | 9.248 | 1/17/2018 | 16:01 | 1.0113 | 1.003
428 | 3867 |  | 17 | 1 |  | 17123 |  | mono-Si module |  |  | OE 939 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.09 | 40.08 | 9.621 | 0.95352 | 32.72 | 0.81637 | 314.8 | 77.8 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-10-02 | 13:22 | PSEL | FLI Proline |  |  |  |  | 8.1 | 41.5 | 6.4 | 2 | 37.8 | 25.6 |  |  |  |  | 2.36 | 2/22/2021 |  | 2/22/2021 |  | PSEL | ./EL/3867_17_1_02222021_80.tiff | ./EL/3867_17_1_02222021_20.tiff | ./IV/3867_17_1_02102021.csv | 0 | 1 | 2 | ./RefIV/3867_17_1_02102021.csv | 8.862 | 8.862 | 7/17/2018 | 15:02 | 1.01 | 1.0002
429 | 3867 |  | 17 | 1 |  | 17123 |  | mono-Si module |  |  | OE 553 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.1 | 40.14 | 9.632 | 0.95366 | 32.86 | 0.81863 | 316.5 | 78.1 | 24.8 | back of panel |  | SPIRE | 4600SLP | 1/21/2020 | 11:29 | PSEL | FLI Proline |  |  |  |  | 8.092 | 41.729 | 6.4 | 2.02 | 37.976 | 56.6 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/3867_17_1_01302020_80.tiff | ./EL/3867_17_1_01302020_20.tiff | ./IV/3867_17_1_01212020.csv | 0 | 0 | 2 | ./RefIV/3867_17_1_01212020.csv | 8.862 | 8.862 | 7/17/2018 | 15:02 | 1.0102 | 1.003
430 | 3876 |  | 17 | 1 |  | 17123 |  | mono-Si module |  |  | OE 1120 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.1 | 40.1 | 9.615 | 0.95198 | 32.76 | 0.81696 | 315 | 77.8 | 25.4 | back of panel |  | SPIRE | 4600SLP | 2021-10-02 | 13:26 | PSEL | FLI Proline |  |  |  |  | 8.1 | 41.5 | 6.4 | 2 | 37.8 | 25.6 |  |  |  |  | 2.36 | 2/22/2021 |  | 2/22/2021 |  | PSEL | ./EL/3876_17_1_02222021_80.tiff | ./EL/3876_17_1_02222021_20.tiff | ./IV/3876_17_1_02102021.csv | 0 | 1 | 2 | ./RefIV/3876_17_1_02102021.csv | 8.862 | 9.248 | 1/17/2018 | 15:49 | 1.0084 | 1.001
431 | 3876 |  | 17 | 1 |  | 17123 |  | mono-Si module |  |  | OE 734 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.09 | 40.17 | 9.622 | 0.95362 | 32.93 | 0.81977 | 316.8 | 78.1 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/21/2020 | 11:16 | PSEL | FLI Proline |  |  |  |  | 8.092 | 41.504 | 6.4 | 2.03 | 37.864 | 25.6 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/3876_17_1_01302020_80.tiff | ./EL/3876_17_1_01302020_20.tiff | ./IV/3876_17_1_01212020.csv | 0 | 0 | 2 | ./RefIV/3876_17_1_01212020.csv | 8.862 | 9.248 | 1/17/2018 | 15:49 | 1.0101 | 1.0044
432 | 3859 |  | 17 | 1 |  | 17123 |  | mono-Si module |  |  | OE 1120 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.1 | 40.13 | 9.637 | 0.95416 | 32.85 | 0.81859 | 316.6 | 78.1 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-10-02 | 13:19 | PSEL | FLI Proline |  |  |  |  | 8.1 | 41.5 | 6.4 | 2 | 37.8 | 25.6 |  |  |  |  | 2.36 | 2/22/2021 |  | 2/22/2021 |  | PSEL | ./EL/3859_17_1_02222021_80.tiff | ./EL/3859_17_1_02222021_20.tiff | ./IV/3859_17_1_02102021.csv | 0 | 1 | 2 | ./RefIV/3859_17_1_02102021.csv | 8.862 | 9.248 | 1/17/2018 | 10:54 | 1.0107 | 1.003
433 | 3859 |  | 17 | 1 |  | 17123 |  | mono-Si module |  |  | OE 734 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.1 | 40.19 | 9.648 | 0.95525 | 32.97 | 0.82035 | 318.1 | 78.3 | 24.8 | back of panel |  | SPIRE | 4600SLP | 1/21/2020 | 11:36 | PSEL | FLI Proline |  |  |  |  | 8.092 | 41.654 | 6.4 | 2.02 | 37.976 | 25.6 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/3859_17_1_01302020_80.tiff | ./EL/3859_17_1_01302020_20.tiff | ./IV/3859_17_1_01212020.csv | 0 | 0 | 2 | ./RefIV/3859_17_1_01212020.csv | 8.862 | 9.248 | 1/17/2018 | 10:54 | 1.0118 | 1.0051
434 | 4166 |  | 17 | 1 |  | 17112.9 |  | mono-Si module |  |  | OE 517 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.13 | 40.02 | 9.643 | 0.95192 | 32.73 | 0.81784 | 315.6 | 77.9 | 24.7 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 13:04 | PSEL | FLI Proline |  |  |  |  | 8.107 | 41.729 | 6.4 | 2.03 | 37.939 | 25.6 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4166_17_1_01302020_80.tiff | ./EL/4166_17_1_01302020_20.tiff | ./IV/4166_17_1_01292020.csv | 0 | 0 | 2 | ./RefIV/4166_17_1_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 15:10 | 1.0083 | 1.002
435 | 4166 |  | 17 | 1 |  | 17102.8 |  | mono-Si module |  |  | OE 889 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.13 | 39.95 | 9.637 | 0.95133 | 32.51 | 0.81377 | 313.4 | 77.4 | 25 | back of panel |  | SPIRE | 4600SLP | 2021-04-02 | 9:57 | PSEL | FLI Proline |  |  |  |  | 8.107 | 41.054 | 6.4 | 2.045 | 37.188 | 25.6 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/4166_17_1_02082021_80.tiff | ./EL/4166_17_1_02082021_20.tiff | ./IV/4166_17_1_02042021.csv | 0 | 1 | 2 | ./RefIV/4166_17_1_02042021.csv | 8.862 | 8.862 | 8/30/2018 | 15:10 | 1.0077 | 0.99705
436 | 4163 |  | 17 | 1 |  | 17112.9 |  | mono-Si module |  |  | OE 517 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.11 | 40.1 | 9.636 | 0.95312 | 32.76 | 0.81696 | 315.7 | 77.9 | 24.7 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 13:05 | PSEL | FLI Proline |  |  |  |  | 8.112 | 41.879 | 6.4 | 2.03 | 38.051 | 25.6 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4163_17_1_01302020_80.tiff | ./EL/4163_17_1_01302020_20.tiff | ./IV/4163_17_1_01292020.csv | 0 | 0 | 2 | ./RefIV/4163_17_1_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 14:40 | 1.0096 | 1.001
437 | 4163 |  | 17 | 1 |  | 17102.8 |  | mono-Si module |  |  | OE 889 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.1 | 40.09 | 9.613 | 0.95178 | 32.52 | 0.81117 | 312.6 | 77.2 | 24.8 | back of panel |  | SPIRE | 4600SLP | 2021-04-02 | 9:58 | PSEL | FLI Proline |  |  |  |  | 8.112 | 41.166 | 6.4 | 2.045 | 37.338 | 25.6 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/4163_17_1_02082021_80.tiff | ./EL/4163_17_1_02082021_20.tiff | ./IV/4163_17_1_02042021.csv | 0 | 1 | 2 | ./RefIV/4163_17_1_02042021.csv | 8.862 | 8.862 | 8/30/2018 | 14:40 | 1.0082 | 0.99387
438 | 4170 |  | 17 | 1 |  | 17112.9 |  | mono-Si module |  |  | OE 517 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.14 | 40.12 | 9.647 | 0.95138 | 32.79 | 0.8173 | 316.3 | 77.8 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 13:13 | PSEL | FLI Proline |  |  |  |  | 8.107 | 41.804 | 6.4 | 2.03 | 38.014 | 25.6 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4170_17_1_01302020_80.tiff | ./EL/4170_17_1_01302020_20.tiff | ./IV/4170_17_1_01292020.csv | 0 | 0 | 2 | ./RefIV/4170_17_1_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 15:22 | 1.0078 | 1.0014
439 | 4170 |  | 17 | 1 |  | 17102.8 |  | mono-Si module |  |  | OE 889 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.13 | 40.1 | 9.638 | 0.95143 | 32.67 | 0.81471 | 314.9 | 77.5 | 24.6 | back of panel |  | SPIRE | 4600SLP | 2021-04-02 | 10:00 | PSEL | FLI Proline |  |  |  |  | 8.107 | 41.129 | 6.4 | 2.045 | 37.376 | 25.6 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/4170_17_1_02082021_80.tiff | ./EL/4170_17_1_02082021_20.tiff | ./IV/4170_17_1_02042021.csv | 0 | 1 | 2 | ./RefIV/4170_17_1_02042021.csv | 8.862 | 8.862 | 8/30/2018 | 15:22 | 1.0078 | 0.99821
440 | 4171 |  | 17 | 1 |  | 17112.9 |  | mono-Si module |  |  | OE 517 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.1 | 40.09 | 9.642 | 0.95465 | 32.83 | 0.81891 | 316.5 | 78.2 | 25 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 13:17 | PSEL | FLI Proline |  |  |  |  | 8.112 | 41.579 | 6.4 | 2.03 | 37.826 | 25.6 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4171_17_1_01302020_80.tiff | ./EL/4171_17_1_01302020_20.tiff | ./IV/4171_17_1_01292020.csv | 0 | 0 | 2 | ./RefIV/4171_17_1_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 15:24 | 1.0112 | 1.0033
441 | 4171 |  | 17 | 1 |  | 17102.8 |  | mono-Si module |  |  | OE 889 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.1 | 40.02 | 9.637 | 0.95416 | 32.66 | 0.81609 | 314.7 | 77.9 | 25.4 | back of panel |  | SPIRE | 4600SLP | 2021-04-02 | 10:04 | PSEL | FLI Proline |  |  |  |  | 8.112 | 41.129 | 6.4 | 2.045 | 37.301 | 25.6 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/4171_17_1_02082021_80.tiff | ./EL/4171_17_1_02082021_20.tiff | ./IV/4171_17_1_02042021.csv | 0 | 1 | 2 | ./RefIV/4171_17_1_02042021.csv | 8.862 | 8.862 | 8/30/2018 | 15:24 | 1.0107 | 0.9999
442 | 4168 |  | 17 | 1 |  | 17112.9 |  | mono-Si module |  |  | OE 517 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.13 | 40.1 | 9.66 | 0.9536 | 32.79 | 0.81771 | 316.8 | 78 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 13:10 | PSEL | FLI Proline |  |  |  |  | 8.112 | 41.879 | 6.4 | 2.03 | 38.089 | 25.6 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4168_17_1_01302020_80.tiff | ./EL/4168_17_1_01302020_20.tiff | ./IV/4168_17_1_01292020.csv | 0 | 0 | 2 | ./RefIV/4168_17_1_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 15:15 | 1.0101 | 1.0019
443 | 4168 |  | 17 | 1 |  | 17102.8 |  | mono-Si module |  |  | OE 889 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.13 | 40.09 | 9.646 | 0.95222 | 32.61 | 0.81342 | 314.6 | 77.5 | 25 | back of panel |  | SPIRE | 4600SLP | 2021-04-02 | 9:59 | PSEL | FLI Proline |  |  |  |  | 8.112 | 41.204 | 6.4 | 2.045 | 37.338 | 25.6 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/4168_17_1_02082021_80.tiff | ./EL/4168_17_1_02082021_20.tiff | ./IV/4168_17_1_02042021.csv | 0 | 1 | 2 | ./RefIV/4168_17_1_02042021.csv | 8.862 | 8.862 | 8/30/2018 | 15:15 | 1.0086 | 0.99662
444 | 4169 |  | 17 | 1 |  | 17112.9 |  | mono-Si module |  |  | OE 517 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.12 | 40.07 | 9.652 | 0.95375 | 32.78 | 0.81807 | 316.4 | 78 | 25 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 13:15 | PSEL | FLI Proline |  |  |  |  | 8.112 | 41.729 | 6.4 | 2.03 | 37.976 | 25.6 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4169_17_1_01302020_80.tiff | ./EL/4169_17_1_01302020_20.tiff | ./IV/4169_17_1_01292020.csv | 0 | 0 | 2 | ./RefIV/4169_17_1_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 15:17 | 1.0103 | 1.0023
445 | 4169 |  | 17 | 1 |  | 17102.8 |  | mono-Si module |  |  | OE 889 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.13 | 39.97 | 9.646 | 0.95222 | 32.54 | 0.81411 | 313.9 | 77.5 | 25.3 | back of panel |  | SPIRE | 4600SLP | 2021-04-02 | 10:04 | PSEL | FLI Proline |  |  |  |  | 8.112 | 40.979 | 6.4 | 2.045 | 37.188 | 25.6 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/4169_17_1_02082021_80.tiff | ./EL/4169_17_1_02082021_20.tiff | ./IV/4169_17_1_02042021.csv | 0 | 1 | 2 | ./RefIV/4169_17_1_02042021.csv | 8.862 | 8.862 | 8/30/2018 | 15:17 | 1.0086 | 0.99747
446 | 4164 |  | 17 | 1 |  | 17112.9 |  | mono-Si module |  |  | OE 517 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.12 | 40.05 | 9.653 | 0.95385 | 32.76 | 0.81798 | 316.2 | 78 | 25.2 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 13:02 | PSEL | FLI Proline |  |  |  |  | 8.112 | 41.767 | 6.4 | 2.025 | 38.014 | 25.6 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4164_17_1_01302020_80.tiff | ./EL/4164_17_1_01302020_20.tiff | ./IV/4164_17_1_01292020.csv | 0 | 0 | 1 | ./RefIV/4164_17_1_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 14:46 | 1.0104 | 1.0022
447 | 4167 |  | 17 | 1 |  | 17112.9 |  | mono-Si module |  |  | OE 517 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.14 | 39.98 | 9.639 | 0.95059 | 32.66 | 0.81691 | 314.8 | 77.7 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 13:12 | PSEL | FLI Proline |  |  |  |  | 8.107 | 41.692 | 6.4 | 2.03 | 37.939 | 25.6 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4167_17_1_01302020_80.tiff | ./EL/4167_17_1_01302020_20.tiff | ./IV/4167_17_1_01292020.csv | 0 | 0 | 2 | ./RefIV/4167_17_1_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 15:12 | 1.0069 | 1.0009
448 | 4167 |  | 17 | 1 |  | 17102.8 |  | mono-Si module |  |  | OE 889 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.13 | 39.97 | 9.633 | 0.95094 | 32.47 | 0.81236 | 312.8 | 77.2 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-04-02 | 10:03 | PSEL | FLI Proline |  |  |  |  | 8.112 | 40.941 | 6.4 | 2.045 | 37.113 | 25.6 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/4167_17_1_02082021_80.tiff | ./EL/4167_17_1_02082021_20.tiff | ./IV/4167_17_1_02042021.csv | 0 | 1 | 2 | ./RefIV/4167_17_1_02042021.csv | 8.862 | 8.862 | 8/30/2018 | 15:12 | 1.0073 | 0.99532
449 | 4172 |  | 17 | 1 |  | 17112.9 |  | mono-Si module |  |  | OE 517 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.11 | 40.15 | 9.662 | 0.95569 | 32.89 | 0.81918 | 317.7 | 78.3 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 13:16 | PSEL | FLI Proline |  |  |  |  | 8.112 | 41.804 | 6.4 | 2.025 | 38.51 | 25.6 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4172_17_1_01302020_80.tiff | ./EL/4172_17_1_01302020_20.tiff | ./IV/4172_17_1_01292020.csv | 0 | 0 | 2 | ./RefIV/4172_17_1_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 15:34 | 1.0123 | 1.0037
450 | 4172 |  | 17 | 1 |  | 17102.8 |  | mono-Si module |  |  | OE 889 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.11 | 40.12 | 9.652 | 0.9547 | 32.76 | 0.81655 | 316.2 | 77.9 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-04-02 | 10:01 | PSEL | FLI Proline |  |  |  |  | 8.112 | 41.204 | 6.4 | 2.045 | 37.376 | 25.6 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/4172_17_1_02082021_80.tiff | ./EL/4172_17_1_02082021_20.tiff | ./IV/4172_17_1_02042021.csv | 0 | 1 | 2 | ./RefIV/4172_17_1_02042021.csv | 8.862 | 8.862 | 8/30/2018 | 15:34 | 1.0113 | 1.0005
451 | 4165 |  | 17 | 1 |  | 17112.9 |  | mono-Si module |  |  | OE 517 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.14 | 40.11 | 9.644 | 0.95108 | 32.82 | 0.81825 | 316.5 | 77.8 | 24.8 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 13:06 | PSEL | FLI Proline |  |  |  |  | 8.112 | 41.879 | 6.4 | 2.03 | 38.089 | 25.6 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4165_17_1_01302020_80.tiff | ./EL/4165_17_1_01302020_20.tiff | ./IV/4165_17_1_01292020.csv | 0 | 0 | 2 | ./RefIV/4165_17_1_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 14:54 | 1.0074 | 1.0025
452 | 4165 |  | 17 | 1 |  | 17102.8 |  | mono-Si module |  |  | OE 889 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.14 | 40.1 | 9.642 | 0.95089 | 32.69 | 0.81521 | 315.2 | 77.5 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-04-02 | 10:02 | PSEL | FLI Proline |  |  |  |  | 8.112 | 41.166 | 6.4 | 2.045 | 37.338 | 25.6 |  |  |  |  | 2.36 | 2021-08-02 |  | 2021-08-02 |  | PSEL | ./EL/4165_17_1_02082021_80.tiff | ./EL/4165_17_1_02082021_20.tiff | ./IV/4165_17_1_02042021.csv | 0 | 1 | 2 | ./RefIV/4165_17_1_02042021.csv | 8.862 | 8.862 | 8/30/2018 | 14:54 | 1.0072 | 0.99882
453 | 3855 |  | 17 | 1 |  | 17123 |  | mono-Si module |  |  | OE 734 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.08 | 40.34 | 9.614 | 0.95377 | 33 | 0.81805 | 317.3 | 78.1 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/21/2020 | 11:19 | PSEL | FLI Proline |  |  |  |  | 8.097 | 41.992 | 6.4 | 2.025 | 38.301 | 19.2 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/3855_17_1_01302020_80.tiff | ./EL/3855_17_1_01302020_20.tiff | ./IV/3855_17_1_01212020.csv | 0 | 0 | 1 | ./RefIV/3855_17_1_01212020.csv | 8.862 | 9.248 | 1/17/2018 | 8:36 | 1.0103 | 1.0023
454 | 4058 |  | 17 | 1 |  | 17123 |  | mono-Si module |  |  | OE 554 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.1 | 40.18 | 9.643 | 0.95475 | 32.95 | 0.82006 | 317.7 | 78.3 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/21/2020 | 11:53 | PSEL | FLI Proline |  |  |  |  | 8.092 | 41.692 | 6.4 | 2.02 | 37.939 | 25.6 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4058_17_1_01302020_80.tiff | ./EL/4058_17_1_01302020_20.tiff | ./IV/4058_17_1_01212020.csv | 0 | 0 | 1 | ./RefIV/4058_17_1_01212020.csv | 8.862 | 8.862 | 7/16/2018 | 15:19 | 1.0113 | 1.0048
455 | 4063 |  | 17 | 1 |  | 17123 |  | mono-Si module |  |  | OE 554 days | 10.19 | 40.8 | 9.62 | 0.94406 | 33.3 | 0.81618 | 320 | 10.12 | 40.15 | 9.649 | 0.95346 | 32.9 | 0.81943 | 317.5 | 78.2 | 24.8 | back of panel |  | SPIRE | 4600SLP | 1/21/2020 | 12:06 | PSEL | FLI Proline |  |  |  |  | 8.09 | 41.192 | 6.4 | 2.02 | 37.976 | 25.6 |  |  |  |  | 2.36 | 1/30/2020 |  | 1/30/2020 |  | PSEL | ./EL/4063_17_1_01302020_80.tiff | ./EL/4063_17_1_01302020_20.tiff | ./IV/4063_17_1_01212020.csv | 0 | 0 | 1 | ./RefIV/4063_17_1_01212020.csv | 8.862 | 8.862 | 7/16/2018 | 15:42 | 1.01 | 1.004
456 | 10329 |  | 34 | 5 |  | 16750 |  | mono-Si module |  |  | OE 1202 days | 8.25 | 37.7 | 7.96 | 0.96485 | 30.8 | 0.81698 | 245 | 8.886 | 37.67 | 8.408 | 0.94621 | 30.38 | 0.80648 | 255.5 | 76.3 | 25 | back of panel |  | SPIRE | 4600SLP | 1/15/2020 | 10:12 | PSEL | FLI Proline |  |  |  |  | 7.144 | 39.215 | 51.2 | [7 empty] | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/10329_34_5_01202020_80.tiff |  | ./IV/10329_34_5_01152020.csv | 0 | 0 | 1 | ./RefIV/10329_34_5_01152020.csv | 8.862 |  | 9/30/2016 | 12:24 | 0.98068 | 0.98715
457 | 10319 |  | 34 | 5 |  | 16750 |  | mono-Si module |  |  | OE 1202 days | 8.25 | 37.7 | 7.96 | 0.96485 | 30.8 | 0.81698 | 245 | 8.795 | 37.66 | 8.37 | 0.95168 | 30.36 | 0.80616 | 254.1 | 76.7 | 25.2 | back of panel |  | SPIRE | 4600SLP | 1/15/2020 | 12:12 | PSEL | FLI Proline |  |  |  |  | 7.139 | 38.764 | 51.2 | 1.745 | 34.786 | 204.6 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/10319_34_5_01202020_80.tiff | ./EL/10319_34_5_01202020_20.tiff | ./IV/10319_34_5_01152020.csv | 0 | 0 | 1 | ./RefIV/10319_34_5_01152020.csv | 8.862 |  | 9/30/2016 | 12:10 | 0.98635 | 0.98676
458 | 2989 |  | 34 | 5 |  | 16750 |  | mono-Si module |  |  | OE 1202 days | 8.25 | 37.7 | 7.96 | 0.96485 | 30.8 | 0.81698 | 245 | 8.855 | 37.66 | 8.404 | 0.94907 | 30.38 | 0.80669 | 255.3 | 76.5 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/15/2020 | 12:32 | PSEL | FLI Proline |  |  |  |  | 7.144 | 39.027 | 51.2 | [7 empty] | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/2989_34_5_01202020_80.tiff |  | ./IV/2989_34_5_01152020.csv | 0 | 0 | 1 | ./RefIV/2989_34_5_01152020.csv | 8.862 |  | 9/30/2016 | 11:15 | 0.98364 | 0.98741
459 | 10332 |  | 34 | 5 |  | 16750 |  | mono-Si module |  |  | OE 1202 days | 8.25 | 37.7 | 7.96 | 0.96485 | 30.8 | 0.81698 | 245 | 8.837 | 37.69 | 8.395 | 0.94998 | 30.41 | 0.80685 | 255.3 | 76.6 | 25 | back of panel |  | SPIRE | 4600SLP | 1/15/2020 | 12:16 | PSEL | FLI Proline |  |  |  |  | 7.144 | 39.327 | 51.2 | 1.875 | 35.12 | 204.6 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/10332_34_5_01202020_80.tiff | ./EL/10332_34_5_01202020_20.tiff | ./IV/10332_34_5_01152020.csv | 0 | 0 | 1 | ./RefIV/10332_34_5_01152020.csv | 8.862 |  | 9/30/2016 | 11:52 | 0.98459 | 0.9876
460 | 10327 |  | 34 | 5 |  | 16750 |  | mono-Si module |  |  | OE 1202 days | 8.25 | 37.7 | 7.96 | 0.96485 | 30.8 | 0.81698 | 245 | 8.826 | 37.63 | 8.38 | 0.94947 | 30.4 | 0.80787 | 254.7 | 76.7 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/15/2020 | 12:19 | PSEL | FLI Proline |  |  |  |  | 7.144 | 39.102 | 51.2 | 1.785 | 35.011 | 204.6 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/10327_34_5_01202020_80.tiff | ./EL/10327_34_5_01202020_20.tiff | ./IV/10327_34_5_01152020.csv | 0 | 0 | 1 | ./RefIV/10327_34_5_01152020.csv | 8.862 |  | 9/30/2016 | 11:42 | 0.98406 | 0.98885
461 | 10328 |  | 34 | 5 |  | 16750 |  | mono-Si module |  |  | OE 1202 days | 8.25 | 37.7 | 7.96 | 0.96485 | 30.8 | 0.81698 | 245 | 8.902 | 37.67 | 8.451 | 0.94934 | 30.4 | 0.80701 | 256.9 | 76.6 | 24.6 | back of panel |  | SPIRE | 4600SLP | 1/15/2020 | 11:37 | PSEL | FLI Proline |  |  |  |  | 7.144 | 39.14 | 51.2 | 1.79 | 35.086 | 204.6 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/10328_34_5_01202020_80.tiff | ./EL/10328_34_5_01202020_20.tiff | ./IV/10328_34_5_01152020.csv | 0 | 0 | 1 | ./RefIV/10328_34_5_01152020.csv | 8.862 |  | 9/30/2016 | 12:00 | 0.98392 | 0.9878
462 | 10321 |  | 34 | 5 |  | 16750 |  | mono-Si module |  |  | OE 1202 days | 8.25 | 37.7 | 7.96 | 0.96485 | 30.8 | 0.81698 | 245 | 8.846 | 37.69 | 8.408 | 0.95049 | 30.42 | 0.80711 | 255.8 | 76.7 | 25 | back of panel |  | SPIRE | 4600SLP | 1/15/2020 | 12:26 | PSEL | FLI Proline |  |  |  |  | 7.139 | 39.215 | 51.2 | 1.785 | 35.124 | 204.6 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/10321_34_5_01202020_80.tiff | ./EL/10321_34_5_01202020_20.tiff | ./IV/10321_34_5_01152020.csv | 0 | 0 | 1 | ./RefIV/10321_34_5_01152020.csv | 8.862 |  | 9/30/2016 | 11:28 | 0.98511 | 0.98792
463 | 10322 |  | 34 | 5 |  | 16750 |  | mono-Si module |  |  | OE 1202 days | 8.25 | 37.7 | 7.96 | 0.96485 | 30.8 | 0.81698 | 245 | 8.864 | 37.66 | 8.382 | 0.94562 | 30.38 | 0.80669 | 254.6 | 76.3 | 25 | back of panel |  | SPIRE | 4600SLP | 1/15/2020 | 12:22 | PSEL | FLI Proline |  |  |  |  | 7.144 | 39.215 | 51.2 | 1.785 | 35.124 | 204.6 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/10322_34_5_01202020_80.tiff | ./EL/10322_34_5_01202020_20.tiff | ./IV/10322_34_5_01152020.csv | 0 | 0 | 1 | ./RefIV/10322_34_5_01152020.csv | 8.862 |  | 9/30/2016 | 11:48 | 0.98007 | 0.98741
464 | 10326 |  | 34 | 5 |  | 16750 |  | mono-Si module |  |  | OE 1202 days | 8.25 | 37.7 | 7.96 | 0.96485 | 30.8 | 0.81698 | 245 | 8.83 | 37.67 | 8.406 | 0.95198 | 30.45 | 0.80834 | 256 | 77 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/15/2020 | 12:30 | PSEL | FLI Proline |  |  |  |  | 7.139 | 39.065 | 51.2 | 1.785 | 34.936 | 204.6 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/10326_34_5_01202020_80.tiff | ./EL/10326_34_5_01202020_20.tiff | ./IV/10326_34_5_01152020.csv | 0 | 0 | 1 | ./RefIV/10326_34_5_01152020.csv | 8.862 |  | 9/30/2016 | 11:32 | 0.98666 | 0.98942
465 | 10333 |  | 34 | 5 |  | 16750 |  | mono-Si module |  |  | OE 1202 days | 8.25 | 37.7 | 7.96 | 0.96485 | 30.8 | 0.81698 | 245 | 8.909 | 37.68 | 8.446 | 0.94803 | 30.4 | 0.80679 | 256.7 | 76.5 | 25 | back of panel |  | SPIRE | 4600SLP | 1/15/2020 | 11:45 | PSEL | FLI Proline |  |  |  |  | 7.139 | 39.215 | 51.2 | 1.79 | 35.124 | 204.6 |  |  |  |  | 2.36 | 1/20/2020 |  | 1/20/2020 |  | PSEL | ./EL/10333_34_5_01202020_80.tiff | ./EL/10333_34_5_01202020_20.tiff | ./IV/10333_34_5_01152020.csv | 0 | 0 | 1 | ./RefIV/10333_34_5_01152020.csv | 8.862 |  | 9/30/2016 | 12:04 | 0.98257 | 0.98754
466 | 4835 |  | 32 | 2 |  | 19793.8 |  | mono-Si module |  |  | OE 43 days | 9.82 | 51.1 | 9.41 | 0.95825 | 42.4 | 0.82975 | 400 | 9.634 | 50.86 | 9.099 | 0.94447 | 42.64 | 0.83838 | 388 | 79.2 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-02-11 | 12:19 | PSEL | FLI Proline |  |  |  |  | 7.694 | 52.206 | 8 | 1.92 | 47.964 | 40 |  |  |  |  | 1.9 | 2021-03-11 |  | 2021-03-11 |  | PSEL | ./EL/4835_32_2_11032021_80.tiff | ./EL/4835_32_2_11032021_20.tiff | ./IV/4835_32_2_11022021.csv | 0 | 0 | 1 | ./RefIV/4835_32_2_11022021.csv | 8.862 | 8.862 | 9/20/2021 | 14:09 | 0.98562 | 1.0104
467 | 4836 |  | 32 | 2 |  | 19793.8 |  | mono-Si module |  |  | OE 43 days | 9.82 | 51.1 | 9.41 | 0.95825 | 42.4 | 0.82975 | 400 | 9.603 | 50.89 | 9.07 | 0.9445 | 42.39 | 0.83297 | 384.5 | 78.7 | 24.8 | back of panel |  | SPIRE | 4600SLP | 2021-02-11 | 12:47 | PSEL | FLI Proline |  |  |  |  | 7.689 | 52.281 | 8 | 1.92 | 48.002 | 40 |  |  |  |  | 1.9 | 2021-02-11 |  | 2021-02-11 |  | PSEL | ./EL/4836_32_2_11022021_80.tiff | ./EL/4836_32_2_11022021_20.tiff | ./IV/4836_32_2_11022021.csv | 0 | 0 | 1 | ./RefIV/4836_32_2_11022021.csv | 8.862 | 8.862 | 9/20/2021 | 14:10 | 0.98565 | 1.0039
468 | 4837 |  | 32 | 2 |  | 19793.8 |  | mono-Si module |  |  | OE 43 days | 9.82 | 51.1 | 9.41 | 0.95825 | 42.4 | 0.82975 | 400 | 9.635 | 50.86 | 9.077 | 0.94209 | 42.27 | 0.8311 | 383.7 | 78.3 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-02-11 | 12:17 | PSEL | FLI Proline |  |  |  |  | 7.689 | 52.393 | 8 | 1.92 | 48.002 | 40 |  |  |  |  | 1.9 | 2021-03-11 |  | 2021-03-11 |  | PSEL | ./EL/4837_32_2_11032021_80.tiff | ./EL/4837_32_2_11032021_20.tiff | ./IV/4837_32_2_11022021.csv | 0 | 0 | 1 | ./RefIV/4837_32_2_11022021.csv | 8.862 | 8.862 | 9/20/2021 | 14:12 | 0.98313 | 1.0016
469 | 4833 |  | 32 | 2 |  | 19793.8 |  | mono-Si module |  |  | OE 43 days | 9.82 | 51.1 | 9.41 | 0.95825 | 42.4 | 0.82975 | 400 | 9.632 | 50.97 | 9.104 | 0.94518 | 42.7 | 0.83775 | 388.8 | 79.2 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-02-11 | 12:23 | PSEL | FLI Proline |  |  |  |  | 7.694 | 52.318 | 8 | 1.915 | 48.002 | 40 |  |  |  |  | 1.9 | 2021-03-11 |  | 2021-03-11 |  | PSEL | ./EL/4833_32_2_11032021_80.tiff | ./EL/4833_32_2_11032021_20.tiff | ./IV/4833_32_2_11022021.csv | 0 | 0 | 1 | ./RefIV/4833_32_2_11022021.csv | 8.862 | 8.862 | 9/20/2021 | 14:04 | 0.98636 | 1.0096
470 | 4838 |  | 32 | 2 |  | 19793.8 |  | mono-Si module |  |  | OE 43 days | 9.82 | 51.1 | 9.41 | 0.95825 | 42.4 | 0.82975 | 400 | 9.607 | 50.86 | 9.097 | 0.94691 | 42.51 | 0.83582 | 386.7 | 79.1 | 24.8 | back of panel |  | SPIRE | 4600SLP | 2021-02-11 | 12:46 | PSEL | FLI Proline |  |  |  |  | 7.689 | 52.206 | 8 | 1.915 | 47.852 | 40 |  |  |  |  | 1.9 | 2021-02-11 |  | 2021-02-11 |  | PSEL | ./EL/4838_32_2_11022021_80.tiff | ./EL/4838_32_2_11022021_20.tiff | ./IV/4838_32_2_11022021.csv | 0 | 0 | 1 | ./RefIV/4838_32_2_11022021.csv | 8.862 | 8.862 | 9/20/2021 | 14:13 | 0.98817 | 1.0073
471 | 4856 |  | 32 | 2 |  | 19793.8 |  | mono-Si module |  |  | OE 0 days | 9.82 | 51.1 | 9.41 | 0.95825 | 42.4 | 0.82975 | 400 | 9.622 | 50.83 | 9.101 | 0.94585 | 42.26 | 0.8314 | 384.6 | 78.6 | 24.6 | back of panel |  | SPIRE | 4600SLP | 2021-02-11 | 12:40 | PSEL | FLI Proline |  |  |  |  | 7.689 | 52.243 | 8 | 1.92 | 47.852 | 40 |  |  |  |  | 1.9 | 2021-02-11 |  | 2021-02-11 |  | PSEL | ./EL/4856_32_2_11022021_80.tiff | ./EL/4856_32_2_11022021_20.tiff | ./IV/4856_32_2_11022021.csv | 0 | 0 | 1 | ./RefIV/4856_32_2_11022021.csv | 8.862 | 8.862 | 2021-02-11 | 12:40 | 0.98706 | 1.002
472 | 4855 |  | 32 | 2 |  | 19793.8 |  | mono-Si module |  |  | OE 0 days | 9.82 | 51.1 | 9.41 | 0.95825 | 42.4 | 0.82975 | 400 | 9.627 | 51 | 9.083 | 0.94349 | 42.49 | 0.83314 | 386 | 78.6 | 24.8 | back of panel |  | SPIRE | 4600SLP | 2021-02-11 | 12:39 | PSEL | FLI Proline |  |  |  |  | 7.694 | 52.431 | 8 | 1.915 | 47.927 | 40 |  |  |  |  | 1.9 | 2021-02-11 |  | 2021-02-11 |  | PSEL | ./EL/4855_32_2_11022021_80.tiff | ./EL/4855_32_2_11022021_20.tiff | ./IV/4855_32_2_11022021.csv | 0 | 0 | 1 | ./RefIV/4855_32_2_11022021.csv | 8.862 | 8.862 | 2021-02-11 | 12:39 | 0.9846 | 1.0041
473 | 4857 |  | 32 | 2 |  | 19793.8 |  | mono-Si module |  |  | OE 0 days | 9.82 | 51.1 | 9.41 | 0.95825 | 42.4 | 0.82975 | 400 | 9.605 | 50.88 | 9.082 | 0.94555 | 42.46 | 0.83451 | 385.6 | 78.9 | 24.6 | back of panel |  | SPIRE | 4600SLP | 2021-02-11 | 12:42 | PSEL | FLI Proline |  |  |  |  | 7.694 | 51.718 | 8 | 1.92 | 47.364 | 40 |  |  |  |  | 1.9 | 2021-02-11 |  | 2021-02-11 |  | PSEL | ./EL/4857_32_2_11022021_80.tiff | ./EL/4857_32_2_11022021_20.tiff | ./IV/4857_32_2_11022021.csv | 0 | 0 | 1 | ./RefIV/4857_32_2_11022021.csv | 8.862 | 8.862 | 2021-02-11 | 12:42 | 0.98675 | 1.0057
474 | 4839 |  | 32 | 2 |  | 19793.8 |  | mono-Si module |  |  | OE 43 days | 9.82 | 51.1 | 9.41 | 0.95825 | 42.4 | 0.82975 | 400 | 9.625 | 50.82 | 9.086 | 0.944 | 42.37 | 0.83373 | 385 | 78.7 | 25.3 | back of panel |  | SPIRE | 4600SLP | 2021-02-11 | 12:15 | PSEL | FLI Proline |  |  |  |  | 7.689 | 52.281 | 8 | 1.925 | 47.814 | 40 |  |  |  |  | 1.9 | 2021-03-11 |  | 2021-03-11 |  | PSEL | ./EL/4839_32_2_11032021_80.tiff | ./EL/4839_32_2_11032021_20.tiff | ./IV/4839_32_2_11022021.csv | 0 | 0 | 1 | ./RefIV/4839_32_2_11022021.csv | 8.862 | 8.862 | 9/20/2021 | 14:15 | 0.98513 | 1.0048
475 | 4841 |  | 32 | 2 |  | 19793.8 |  | mono-Si module |  |  | OE 43 days | 9.82 | 51.1 | 9.41 | 0.95825 | 42.4 | 0.82975 | 400 | 9.611 | 50.86 | 9.072 | 0.94392 | 42.3 | 0.83169 | 383.8 | 78.5 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-02-11 | 12:13 | PSEL | FLI Proline |  |  |  |  | 7.694 | 52.356 | 8 | 1.915 | 47.964 | 40 |  |  |  |  | 1.9 | 2021-03-11 |  | 2021-03-11 |  | PSEL | ./EL/4841_32_2_11032021_80.tiff | ./EL/4841_32_2_11032021_20.tiff | ./IV/4841_32_2_11022021.csv | 0 | 0 | 1 | ./RefIV/4841_32_2_11022021.csv | 8.862 | 8.862 | 9/20/2021 | 13:46 | 0.98505 | 1.0023
476 | 4846 |  | 32 | 2 |  | 19793.8 |  | mono-Si module |  |  | OE 0 days | 9.82 | 51.1 | 9.41 | 0.95825 | 42.4 | 0.82975 | 400 | 9.619 | 50.91 | 9.079 | 0.94386 | 42.27 | 0.83029 | 383.7 | 78.4 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-02-11 | 12:24 | PSEL | FLI Proline |  |  |  |  | 7.689 | 52.393 | 8 | 1.92 | 48.039 | 40 |  |  |  |  | 1.9 | 2021-03-11 |  | 2021-03-11 |  | PSEL | ./EL/4846_32_2_11032021_80.tiff | ./EL/4846_32_2_11032021_20.tiff | ./IV/4846_32_2_11022021.csv | 0 | 0 | 1 | ./RefIV/4846_32_2_11022021.csv | 8.862 | 8.862 | 2021-02-11 | 12:24 | 0.98499 | 1.0007
477 | 4848 |  | 32 | 2 |  | 19793.8 |  | mono-Si module |  |  | OE 0 days | 9.82 | 51.1 | 9.41 | 0.95825 | 42.4 | 0.82975 | 400 | 9.61 | 50.82 | 9.075 | 0.94433 | 42.48 | 0.83589 | 385.6 | 78.9 | 25.3 | back of panel |  | SPIRE | 4600SLP | 2021-02-11 | 12:30 | PSEL | FLI Proline |  |  |  |  | 7.689 | 52.168 | 8 | 1.92 | 47.889 | 40 |  |  |  |  | 1.9 | 2021-03-11 |  | 2021-03-11 |  | PSEL | ./EL/4848_32_2_11032021_80.tiff | ./EL/4848_32_2_11032021_20.tiff | ./IV/4848_32_2_11022021.csv | 0 | 0 | 1 | ./RefIV/4848_32_2_11022021.csv | 8.862 | 8.862 | 2021-02-11 | 12:30 | 0.98547 | 1.0074
478 | 4854 |  | 32 | 2 |  | 19793.8 |  | mono-Si module |  |  | OE 0 days | 9.82 | 51.1 | 9.41 | 0.95825 | 42.4 | 0.82975 | 400 | 9.616 | 50.84 | 9.09 | 0.9453 | 42.42 | 0.83438 | 385.6 | 78.9 | 24.8 | back of panel |  | SPIRE | 4600SLP | 2021-02-11 | 12:37 | PSEL | FLI Proline |  |  |  |  | 7.689 | 52.13 | 8 | 1.92 | 47.889 | 40 |  |  |  |  | 1.9 | 2021-02-11 |  | 2021-02-11 |  | PSEL | ./EL/4854_32_2_11022021_80.tiff | ./EL/4854_32_2_11022021_20.tiff | ./IV/4854_32_2_11022021.csv | 0 | 0 | 1 | ./RefIV/4854_32_2_11022021.csv | 8.862 | 8.862 | 2021-02-11 | 12:37 | 0.98649 | 1.0056
479 | 4843 |  | 32 | 2 |  | 19793.8 |  | mono-Si module |  |  | OE 43 days | 9.82 | 51.1 | 9.41 | 0.95825 | 42.4 | 0.82975 | 400 | 9.628 | 50.86 | 9.081 | 0.94319 | 42.21 | 0.82993 | 383.3 | 78.3 | 25.4 | back of panel |  | SPIRE | 4600SLP | 2021-02-11 | 12:10 | PSEL | FLI Proline |  |  |  |  | 7.689 | 52.468 | 8 | 1.92 | 47.927 | 40 |  |  |  |  | 1.9 | 2021-03-11 |  | 2021-03-11 |  | PSEL | ./EL/4843_32_2_11032021_80.tiff | ./EL/4843_32_2_11032021_20.tiff | ./IV/4843_32_2_11022021.csv | 0 | 0 | 1 | ./RefIV/4843_32_2_11022021.csv | 8.862 | 8.862 | 9/20/2021 | 13:54 | 0.98428 | 1.0002
480 | 4840 |  | 32 | 2 |  | 19793.8 |  | mono-Si module |  |  | OE 43 days | 9.82 | 51.1 | 9.41 | 0.95825 | 42.4 | 0.82975 | 400 | 9.604 | 50.87 | 9.093 | 0.94679 | 42.36 | 0.83271 | 385.2 | 78.8 | 24.7 | back of panel |  | SPIRE | 4600SLP | 2021-02-11 | 12:45 | PSEL | FLI Proline |  |  |  |  | 7.689 | 52.318 | 8 | 1.92 | 47.927 | 40 |  |  |  |  | 1.9 | 2021-02-11 |  | 2021-02-11 |  | PSEL | ./EL/4840_32_2_11022021_80.tiff | ./EL/4840_32_2_11022021_20.tiff | ./IV/4840_32_2_11022021.csv | 0 | 0 | 1 | ./RefIV/4840_32_2_11022021.csv | 8.862 | 8.862 | 9/20/2021 | 14:16 | 0.98805 | 1.0036
481 | 4850 |  | 32 | 2 |  | 19793.8 |  | mono-Si module |  |  | OE 0 days | 9.82 | 51.1 | 9.41 | 0.95825 | 42.4 | 0.82975 | 400 | 9.604 | 50.75 | 9.075 | 0.94492 | 42.4 | 0.83547 | 384.8 | 79 | 25.3 | back of panel |  | SPIRE | 4600SLP | 2021-02-11 | 12:34 | PSEL | FLI Proline |  |  |  |  | 7.689 | 52.206 | 8 | 1.92 | 47.889 | 40 |  |  |  |  | 1.9 | 2021-02-11 |  | 2021-02-11 |  | PSEL | ./EL/4850_32_2_11022021_80.tiff | ./EL/4850_32_2_11022021_20.tiff | ./IV/4850_32_2_11022021.csv | 0 | 0 | 1 | ./RefIV/4850_32_2_11022021.csv | 8.862 | 8.862 | 2021-02-11 | 12:34 | 0.98609 | 1.0069
482 | 4831 |  | 32 | 2 |  | 19793.8 |  | mono-Si module |  |  | OE 43 days | 9.82 | 51.1 | 9.41 | 0.95825 | 42.4 | 0.82975 | 400 | 9.626 | 50.96 | 9.105 | 0.94588 | 42.71 | 0.83811 | 388.9 | 79.3 | 24.7 | back of panel |  | SPIRE | 4600SLP | 2021-02-11 | 12:49 | PSEL | FLI Proline |  |  |  |  | 7.689 | 52.206 | 8 | 1.915 | 47.889 | 40 |  |  |  |  | 1.9 | 2021-02-11 |  | 2021-02-11 |  | PSEL | ./EL/4831_32_2_11022021_80.tiff | ./EL/4831_32_2_11022021_20.tiff | ./IV/4831_32_2_11022021.csv | 0 | 0 | 1 | ./RefIV/4831_32_2_11022021.csv | 8.862 | 8.862 | 9/20/2021 | 14:00 | 0.98709 | 1.0101
483 | 4845 |  | 32 | 2 |  | 19793.8 |  | mono-Si module |  |  | OE 43 days | 9.82 | 51.1 | 9.41 | 0.95825 | 42.4 | 0.82975 | 400 | 9.595 | 50.84 | 9.082 | 0.94653 | 42.29 | 0.83183 | 384.1 | 78.7 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-02-11 | 12:35 | PSEL | FLI Proline |  |  |  |  | 7.689 | 52.393 | 8 | 1.915 | 47.889 | 40 |  |  |  |  | 1.9 | 2021-02-11 |  | 2021-02-11 |  | PSEL | ./EL/4845_32_2_11022021_80.tiff | ./EL/4845_32_2_11022021_20.tiff | ./IV/4845_32_2_11022021.csv | 0 | 0 | 1 | ./RefIV/4845_32_2_11022021.csv | 8.862 | 8.862 | 9/20/2021 | 13:57 | 0.98778 | 1.0025
484 | 4832 |  | 32 | 2 |  | 19793.8 |  | mono-Si module |  |  | OE 43 days | 9.82 | 51.1 | 9.41 | 0.95825 | 42.4 | 0.82975 | 400 | 9.638 | 50.98 | 9.102 | 0.94439 | 42.69 | 0.83739 | 388.6 | 79.1 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-02-11 | 12:21 | PSEL | FLI Proline |  |  |  |  | 7.689 | 52.281 | 8 | 1.915 | 48.114 | 40 |  |  |  |  | 1.9 | 2021-03-11 |  | 2021-03-11 |  | PSEL | ./EL/4832_32_2_11032021_80.tiff | ./EL/4832_32_2_11032021_20.tiff | ./IV/4832_32_2_11022021.csv | 0 | 0 | 1 | ./RefIV/4832_32_2_11022021.csv | 8.862 | 8.862 | 9/20/2021 | 14:02 | 0.98553 | 1.0092
485 | 4844 |  | 32 | 2 |  | 19793.8 |  | mono-Si module |  |  | OE 43 days | 9.82 | 51.1 | 9.41 | 0.95825 | 42.4 | 0.82975 | 400 | 9.613 | 50.92 | 9.087 | 0.94528 | 42.31 | 0.83091 | 384.5 | 78.6 | 24.6 | back of panel |  | SPIRE | 4600SLP | 2021-02-11 | 12:43 | PSEL | FLI Proline |  |  |  |  | 7.689 | 52.393 | 4 | 1.92 | 48.039 | 40 |  |  |  |  | 1.9 | 2021-02-11 |  | 2021-02-11 |  | PSEL | ./EL/4844_32_2_11022021_80.tiff | ./EL/4844_32_2_11022021_20.tiff | ./IV/4844_32_2_11022021.csv | 0 | 0 | 1 | ./RefIV/4844_32_2_11022021.csv | 8.862 | 8.862 | 9/20/2021 | 13:55 | 0.98647 | 1.0014
486 | 4849 |  | 32 | 2 |  | 19793.8 |  | mono-Si module |  |  | OE 0 days | 9.82 | 51.1 | 9.41 | 0.95825 | 42.4 | 0.82975 | 400 | 9.589 | 50.85 | 9.069 | 0.94577 | 42.29 | 0.83166 | 383.5 | 78.7 | 25.4 | back of panel |  | SPIRE | 4600SLP | 2021-02-11 | 12:32 | PSEL | FLI Proline |  |  |  |  | 7.689 | 52.206 | 8 | 1.92 | 47.701 | 40 |  |  |  |  | 1.9 | 2021-03-11 |  | 2021-03-11 |  | PSEL | ./EL/4849_32_2_11032021_80.tiff | ./EL/4849_32_2_11032021_20.tiff | ./IV/4849_32_2_11022021.csv | 0 | 0 | 2 | ./RefIV/4849_32_2_11022021.csv | 8.862 | 8.862 | 2021-02-11 | 12:32 | 0.98698 | 1.0023
487 | 4849 |  | 32 | 2 |  | 19793.8 |  | mono-Si module |  |  | OE 0 days | 9.82 | 51.1 | 9.41 | 0.95825 | 42.4 | 0.82975 | 400 | 9.589 | 50.85 | 9.069 | 0.94577 | 42.29 | 0.83166 | 383.5 | 78.7 | 25.4 | back of panel |  | SPIRE | 4600SLP | 2021-02-11 | 12:32 | PSEL | FLI Proline |  |  |  |  | 7.694 | 52.431 | 8 | 1.92 | 47.964 | 40 |  |  |  |  | 1.9 | 2021-02-11 |  | 2021-02-11 |  | PSEL | ./EL/4849_32_2_11022021_80.tiff | ./EL/4849_32_2_11022021_20.tiff | ./IV/4849_32_2_11022021.csv | 0 | 1 | 2 | ./RefIV/4849_32_2_11022021.csv | 8.862 | 8.862 | 2021-02-11 | 12:32 | 0.98698 | 1.0023
488 | 4842 |  | 32 | 2 |  | 19793.8 |  | mono-Si module |  |  | OE 43 days | 9.82 | 51.1 | 9.41 | 0.95825 | 42.4 | 0.82975 | 400 | 9.617 | 51.03 | 9.081 | 0.94427 | 42.43 | 0.83147 | 385.3 | 78.5 | 24.6 | back of panel |  | SPIRE | 4600SLP | 2021-02-11 | 12:44 | PSEL | FLI Proline |  |  |  |  | 7.689 | 52.506 | 8 | 1.92 | 47.964 | 40 |  |  |  |  | 1.9 | 2021-02-11 |  | 2021-02-11 |  | PSEL | ./EL/4842_32_2_11022021_80.tiff | ./EL/4842_32_2_11022021_20.tiff | ./IV/4842_32_2_11022021.csv | 0 | 0 | 1 | ./RefIV/4842_32_2_11022021.csv | 8.862 | 8.862 | 9/20/2021 | 13:52 | 0.98541 | 1.0021
489 | 4847 |  | 32 | 2 |  | 19793.8 |  | mono-Si module |  |  | OE 0 days | 9.82 | 51.1 | 9.41 | 0.95825 | 42.4 | 0.82975 | 400 | 9.64 | 50.78 | 9.098 | 0.94378 | 42.36 | 0.83419 | 385.4 | 78.7 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-02-11 | 12:26 | PSEL | FLI Proline |  |  |  |  | 7.694 | 52.206 | 8 | 1.915 | 47.776 | 40 |  |  |  |  | 1.9 | 2021-03-11 |  | 2021-03-11 |  | PSEL | ./EL/4847_32_2_11032021_80.tiff | ./EL/4847_32_2_11032021_20.tiff | ./IV/4847_32_2_11022021.csv | 0 | 0 | 1 | ./RefIV/4847_32_2_11022021.csv | 8.862 | 8.862 | 2021-02-11 | 12:26 | 0.9849 | 1.0054
490 | 4851 |  | 32 | 2 |  | 19793.8 |  | mono-Si module |  |  | OE 0 days | 9.82 | 51.1 | 9.41 | 0.95825 | 42.4 | 0.82975 | 400 | 9.631 | 50.84 | 9.096 | 0.94445 | 42.45 | 0.83497 | 386.2 | 78.9 | 25 | back of panel |  | SPIRE | 4600SLP | 2021-02-11 | 12:36 | PSEL | FLI Proline |  |  |  |  | 7.694 | 52.168 | 8 | 1.92 | 47.739 | 40 |  |  |  |  | 1.9 | 2021-02-11 |  | 2021-02-11 |  | PSEL | ./EL/4851_32_2_11022021_80.tiff | ./EL/4851_32_2_11022021_20.tiff | ./IV/4851_32_2_11022021.csv | 0 | 0 | 1 | ./RefIV/4851_32_2_11022021.csv | 8.862 | 8.862 | 2021-02-11 | 12:36 | 0.9856 | 1.0063
491 | 4896 |  | 32 | 2 |  | 19793.8 |  | mono-Si module |  |  | OE 0 days | 9.82 | 51.1 | 9.41 | 0.95825 | 42.4 | 0.82975 | 400 | 9.627 | 51.02 | 9.104 | 0.94567 | 42.6 | 0.83497 | 387.8 | 79 | 25.4 | back of panel |  | SPIRE | 4600SLP | 10/26/2021 | 10:09 | PSEL | FLI Proline |  |  |  |  | 7.229 | 52.018 | 8 | 1.915 | 47.814 | 40 |  |  |  |  | 1.9 | 10/26/2021 |  | 10/26/2021 |  | PSEL | ./EL/4896_32_2_10262021_80.tiff | ./EL/4896_32_2_10262021_20.tiff | ./IV/4896_32_2_10262021.csv | 0 | 0 | 1 | ./RefIV/4896_32_2_10262021.csv | 8.862 | 8.862 | 10/26/2021 | 10:09 | 0.98688 | 1.0063
492 | 4152 |  | 5 | 8 |  | 16335 |  | mono-Si module |  |  | OE 517 days | 9.83 | 39.7 | 9.24 | 0.93998 | 32.5 | 0.81864 | 300 | 9.635 | 39.56 | 9.211 | 0.95599 | 31.94 | 0.80738 | 294.2 | 77.2 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 10:01 | PSEL | FLI Proline |  |  |  |  | 7.723 | 41.504 | 9.6 | 1.935 | 37.376 | 51.2 |  |  |  |  | 2.36 | 1/29/2020 |  | 1/29/2020 |  | PSEL | ./EL/4152_5_8_01292020_80.tiff | ./EL/4152_5_8_01292020_20.tiff | ./IV/4152_5_8_01292020.csv | 0 | 0 | 1 | ./RefIV/4152_5_8_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 12:50 | 1.017 | 0.98625
493 | 4160 |  | 5 | 8 |  | 16335 |  | mono-Si module |  |  | OE 517 days | 9.83 | 39.7 | 9.24 | 0.93998 | 32.5 | 0.81864 | 300 | 9.61 | 39.56 | 9.173 | 0.95453 | 31.89 | 0.80612 | 292.5 | 76.9 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 9:57 | PSEL | FLI Proline |  |  |  |  | 7.718 | 41.467 | 9.6 | 1.935 | 37.263 | 51.2 |  |  |  |  | 2.36 | 1/29/2020 |  | 1/29/2020 |  | PSEL | ./EL/4160_5_8_01292020_80.tiff | ./EL/4160_5_8_01292020_20.tiff | ./IV/4160_5_8_01292020.csv | 0 | 0 | 1 | ./RefIV/4160_5_8_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 13:44 | 1.0155 | 0.9847
494 | 4155 |  | 5 | 8 |  | 16335 |  | mono-Si module |  |  | OE 517 days | 9.83 | 39.7 | 9.24 | 0.93998 | 32.5 | 0.81864 | 300 | 9.627 | 39.58 | 9.215 | 0.9572 | 32.05 | 0.80975 | 295.3 | 77.5 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 10:08 | PSEL | FLI Proline |  |  |  |  | 7.723 | 41.241 | 9.6 | 1.935 | 37.151 | 51.2 |  |  |  |  | 2.36 | 1/29/2020 |  | 1/29/2020 |  | PSEL | ./EL/4155_5_8_01292020_80.tiff | ./EL/4155_5_8_01292020_20.tiff | ./IV/4155_5_8_01292020.csv | 0 | 0 | 1 | ./RefIV/4155_5_8_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 13:23 | 1.0183 | 0.98914
495 | 4156 |  | 5 | 8 |  | 16335 |  | mono-Si module |  |  | OE 517 days | 9.83 | 39.7 | 9.24 | 0.93998 | 32.5 | 0.81864 | 300 | 9.643 | 39.61 | 9.225 | 0.95665 | 32.02 | 0.80838 | 295.4 | 77.3 | 25 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 10:06 | PSEL | FLI Proline |  |  |  |  | 7.723 | 41.241 | 9.6 | 1.935 | 37.151 | 51.2 |  |  |  |  | 2.36 | 1/29/2020 |  | 1/29/2020 |  | PSEL | ./EL/4156_5_8_01292020_80.tiff | ./EL/4156_5_8_01292020_20.tiff | ./IV/4156_5_8_01292020.csv | 0 | 0 | 1 | ./RefIV/4156_5_8_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 13:26 | 1.0177 | 0.98747
496 | 4157 |  | 5 | 8 |  | 16335 |  | mono-Si module |  |  | OE 517 days | 9.83 | 39.7 | 9.24 | 0.93998 | 32.5 | 0.81864 | 300 | 9.642 | 39.59 | 9.202 | 0.95437 | 32.11 | 0.81106 | 295.5 | 77.4 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 9:55 | PSEL | FLI Proline |  |  |  |  | 7.718 | 41.504 | 9.6 | 1.935 | 37.075 | 9.6 |  |  |  |  | 2.36 | 1/29/2020 |  | 1/29/2020 |  | PSEL | ./EL/4157_5_8_01292020_80.tiff | ./EL/4157_5_8_01292020_20.tiff | ./IV/4157_5_8_01292020.csv | 0 | 0 | 1 | ./RefIV/4157_5_8_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 13:29 | 1.0153 | 0.99075
497 | 4153 |  | 5 | 8 |  | 16335 |  | mono-Si module |  |  | OE 517 days | 9.83 | 39.7 | 9.24 | 0.93998 | 32.5 | 0.81864 | 300 | 9.627 | 39.53 | 9.2 | 0.95565 | 32.03 | 0.81027 | 294.6 | 77.4 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 10:05 | PSEL | FLI Proline |  |  |  |  | 7.723 | 41.421 | 9.6 | 1.93 | 37.236 | 51.2 |  |  |  |  | 2.36 | 1/29/2020 |  | 1/29/2020 |  | PSEL | ./EL/4153_5_8_01292020_80.tiff | ./EL/4153_5_8_01292020_20.tiff | ./IV/4153_5_8_01292020.csv | 0 | 0 | 1 | ./RefIV/4153_5_8_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 13:09 | 1.0167 | 0.98978
498 | 4151 |  | 5 | 8 |  | 16335 |  | mono-Si module |  |  | OE 517 days | 9.83 | 39.7 | 9.24 | 0.93998 | 32.5 | 0.81864 | 300 | 9.644 | 39.6 | 9.212 | 0.95521 | 31.96 | 0.80707 | 294.4 | 77.1 | 25 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 10:02 | PSEL | FLI Proline |  |  |  |  | 7.723 | 41.204 | 9.6 | 1.935 | 37.113 | 51.2 |  |  |  |  | 2.36 | 1/29/2020 |  | 1/29/2020 |  | PSEL | ./EL/4151_5_8_01292020_80.tiff | ./EL/4151_5_8_01292020_20.tiff | ./IV/4151_5_8_01292020.csv | 0 | 0 | 1 | ./RefIV/4151_5_8_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 12:44 | 1.0162 | 0.98587
499 | 4154 |  | 5 | 8 |  | 16335 |  | mono-Si module |  |  | OE 517 days | 9.83 | 39.7 | 9.24 | 0.93998 | 32.5 | 0.81864 | 300 | 9.66 | 39.56 | 9.231 | 0.95559 | 32.01 | 0.80915 | 295.5 | 77.3 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 10:03 | PSEL | FLI Proline |  |  |  |  | 7.728 | 41.091 | 9.6 | 1.935 | 36.925 | 51.2 |  |  |  |  | 2.36 | 1/29/2020 |  | 1/29/2020 |  | PSEL | ./EL/4154_5_8_01292020_80.tiff | ./EL/4154_5_8_01292020_20.tiff | ./IV/4154_5_8_01292020.csv | 0 | 0 | 1 | ./RefIV/4154_5_8_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 13:12 | 1.0166 | 0.98841
500 | 4158 |  | 5 | 8 |  | 16335 |  | mono-Si module |  |  | OE 517 days | 9.83 | 39.7 | 9.24 | 0.93998 | 32.5 | 0.81864 | 300 | 9.644 | 39.56 | 9.217 | 0.95572 | 31.87 | 0.80561 | 293.7 | 77 | 25 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 10:09 | PSEL | FLI Proline |  |  |  |  | 7.723 | 41.241 | 9.6 | 1.935 | 36.963 | 51.2 |  |  |  |  | 2.36 | 1/29/2020 |  | 1/29/2020 |  | PSEL | ./EL/4158_5_8_01292020_80.tiff | ./EL/4158_5_8_01292020_20.tiff | ./IV/4158_5_8_01292020.csv | 0 | 0 | 1 | ./RefIV/4158_5_8_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 13:33 | 1.0167 | 0.98409
501 | 4159 |  | 5 | 8 |  | 16335 |  | mono-Si module |  |  | OE 517 days | 9.83 | 39.7 | 9.24 | 0.93998 | 32.5 | 0.81864 | 300 | 9.649 | 39.59 | 9.21 | 0.9545 | 32.01 | 0.80854 | 294.8 | 77.2 | 25.1 | back of panel |  | SPIRE | 4600SLP | 1/29/2020 | 9:59 | PSEL | FLI Proline |  |  |  |  | 7.718 | 41.504 | 9.6 | 1.93 | 37.301 | 51.2 |  |  |  |  | 2.36 | 1/29/2020 |  | 1/29/2020 |  | PSEL | ./EL/4159_5_8_01292020_80.tiff | ./EL/4159_5_8_01292020_20.tiff | ./IV/4159_5_8_01292020.csv | 0 | 0 | 1 | ./RefIV/4159_5_8_01292020.csv | 8.862 | 8.862 | 8/30/2018 | 13:37 | 1.0155 | 0.98766
502 | 3713 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 1281 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.179 | 38.05 | 8.71 | 0.94891 | 30.85 | 0.81078 | 268.7 | 76.9 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 15:37 | PSEL | FLI Proline |  |  |  |  | 7.338 | 38.99 | 38.4 | 1.835 | 35.011 | 153.6 |  |  |  |  | 2.36 | 2021-02-02 |  | 2021-02-02 |  | PSEL | ./EL/3713_5_5_02022021_80.tiff | ./EL/3713_5_5_02022021_20.tiff | ./IV/3713_5_5_02012021.csv | 0 | 1 | 2 | ./RefIV/3713_5_5_02012021.csv | 8.862 | 9.0256 | 7/31/2017 | 14:33 | 1.0107 | 0.99767
503 | 3713 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 899 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.189 | 38.08 | 8.726 | 0.94961 | 30.99 | 0.81381 | 270.4 | 77.3 | 24.8 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 10:03 | PSEL | FLI Proline |  |  |  |  | 7.358 | 39.47 | 38.4 | 1.84 | 35.499 | 153.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3713_5_5_01172020_80.tiff | ./EL/3713_5_5_01172020_20.tiff | ./IV/3713_5_5_01162020.csv | 0 | 0 | 2 | ./RefIV/3713_5_5_01162020.csv | 8.862 | 9.0256 | 7/31/2017 | 14:33 | 1.0115 | 1.0014
504 | 3706 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 1281 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.145 | 37.91 | 8.675 | 0.94861 | 30.78 | 0.81192 | 267 | 77 | 24.7 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 15:34 | PSEL | FLI Proline |  |  |  |  | 7.333 | 38.952 | 38.4 | 1.835 | 34.974 | 153.6 |  |  |  |  | 2.36 | 2021-02-02 |  | 2021-02-02 |  | PSEL | ./EL/3706_5_5_02022021_80.tiff | ./EL/3706_5_5_02022021_20.tiff | ./IV/3706_5_5_02012021.csv | 0 | 0 | 1 | ./RefIV/3706_5_5_02012021.csv | 8.862 | 9.0256 | 7/31/2017 | 14:56 | 1.0104 | 0.99909
505 | 3689 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 1281 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.154 | 37.92 | 8.677 | 0.94789 | 30.56 | 0.80591 | 265.2 | 76.4 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 15:19 | PSEL | FLI Proline |  |  |  |  | 7.338 | 39.103 | 38.4 | 1.835 | 35.49 | 150.6 |  |  |  |  | 2.36 | 2021-02-02 |  | 2021-02-02 |  | PSEL | ./EL/3689_5_5_02022021_80.tiff | ./EL/3689_5_5_02022021_20.tiff | ./IV/3689_5_5_02012021.csv | 0 | 1 | 2 | ./RefIV/3689_5_5_02012021.csv | 8.862 | 9.0256 | 7/31/2017 | 10:54 | 1.0096 | 0.99168
506 | 3689 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 899 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.181 | 38.01 | 8.708 | 0.94848 | 30.91 | 0.81321 | 269.2 | 77.1 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 10:25 | PSEL | FLI Proline |  |  |  |  | 7.358 | 39.177 | 38.4 | 1.84 | 35.274 | 153.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3689_5_5_01172020_80.tiff | ./EL/3689_5_5_01172020_20.tiff | ./IV/3689_5_5_01162020.csv | 0 | 0 | 2 | ./RefIV/3689_5_5_01162020.csv | 8.862 | 9.0256 | 7/31/2017 | 10:54 | 1.0103 | 1.0007
507 | 3709 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 1281 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.177 | 38 | 8.706 | 0.94868 | 30.77 | 0.80974 | 267.9 | 76.8 | 24.8 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 15:36 | PSEL | FLI Proline |  |  |  |  | 7.338 | 39.177 | 38.4 | 1.835 | 35.274 | 153.6 |  |  |  |  | 2.36 | 2021-02-02 |  | 2021-02-02 |  | PSEL | ./EL/3709_5_5_02022021_80.tiff | ./EL/3709_5_5_02022021_20.tiff | ./IV/3709_5_5_02012021.csv | 0 | 1 | 2 | ./RefIV/3709_5_5_02012021.csv | 8.862 | 9.0256 | 7/31/2017 | 14:46 | 1.0105 | 0.9964
508 | 3709 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 899 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.191 | 38.07 | 8.724 | 0.94919 | 31.03 | 0.81508 | 270.7 | 77.4 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 10:08 | PSEL | FLI Proline |  |  |  |  | 7.358 | 39.215 | 38.4 | 1.84 | 35.4 | 3072 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3709_5_5_01172020_80.tiff | ./EL/3709_5_5_01172020_20.tiff | ./IV/3709_5_5_01162020.csv | 0 | 0 | 2 | ./RefIV/3709_5_5_01162020.csv | 8.862 | 9.0256 | 7/31/2017 | 14:46 | 1.011 | 1.003
509 | 3685 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 1281 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.15 | 37.92 | 8.657 | 0.94612 | 30.62 | 0.80749 | 265.1 | 76.4 | 24.7 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 15:21 | PSEL | FLI Proline |  |  |  |  | 7.338 | 39.065 | 38.4 | 1.835 | 34.936 | 153.6 |  |  |  |  | 2.36 | 2021-02-02 |  | 2021-02-02 |  | PSEL | ./EL/3685_5_5_02022021_80.tiff | ./EL/3685_5_5_02022021_20.tiff | ./IV/3685_5_5_02012021.csv | 0 | 1 | 2 | ./RefIV/3685_5_5_02012021.csv | 8.862 | 9.0256 | 7/31/2017 | 11:08 | 1.0078 | 0.99363
510 | 3685 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 899 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.158 | 37.99 | 8.685 | 0.94835 | 30.91 | 0.81364 | 268.5 | 77.2 | 24.8 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 10:27 | PSEL | FLI Proline |  |  |  |  | 7.358 | 39.215 | 38.4 | 1.845 | 35.199 | 153.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3685_5_5_01172020_80.tiff | ./EL/3685_5_5_01172020_20.tiff | ./IV/3685_5_5_01162020.csv | 0 | 0 | 2 | ./RefIV/3685_5_5_01162020.csv | 8.862 | 9.0256 | 7/31/2017 | 11:08 | 1.0101 | 1.0012
511 | 3675 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 1281 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.159 | 37.97 | 8.675 | 0.94716 | 30.59 | 0.80564 | 265.4 | 76.3 | 24.6 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 15:23 | PSEL | FLI Proline |  |  |  |  | 7.338 | 39.402 | 38.4 | 1.835 | 35.199 | 153.6 |  |  |  |  | 2.36 | 2021-02-02 |  | 2021-02-02 |  | PSEL | ./EL/3675_5_5_02022021_80.tiff | ./EL/3675_5_5_02022021_20.tiff | ./IV/3675_5_5_02012021.csv | 0 | 1 | 2 | ./RefIV/3675_5_5_02012021.csv | 8.862 | 9.0256 | 7/31/2017 | 11:52 | 1.0089 | 0.99135
512 | 3675 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 899 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.181 | 38.04 | 8.704 | 0.94804 | 31 | 0.81493 | 269.8 | 77.2 | 24.7 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 10:30 | PSEL | FLI Proline |  |  |  |  | 7.358 | 39.29 | 38.4 | 1.845 | 35.349 | 51.2 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3675_5_5_01172020_80.tiff | ./EL/3675_5_5_01172020_20.tiff | ./IV/3675_5_5_01162020.csv | 0 | 0 | 2 | ./RefIV/3675_5_5_01162020.csv | 8.862 | 9.0256 | 7/31/2017 | 11:52 | 1.0098 | 1.0028
513 | 3699 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 1280 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.177 | 37.95 | 8.687 | 0.94661 | 30.6 | 0.80632 | 265.8 | 76.3 | 24.7 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 15:24 | PSEL | FLI Proline |  |  |  |  | 7.338 | 39.252 | 38.4 | 1.835 | 39.252 | 153.6 |  |  |  |  | 2.36 | 2021-02-02 |  | 2021-02-02 |  | PSEL | ./EL/3699_5_5_02022021_80.tiff | ./EL/3699_5_5_02022021_20.tiff | ./IV/3699_5_5_02012021.csv | 0 | 1 | 2 | ./RefIV/3699_5_5_02012021.csv | 8.862 | 9.0256 | 2017-01-08 | 8:07 | 1.0083 | 0.9922
514 | 3699 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 898 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.184 | 38.01 | 8.708 | 0.94817 | 30.87 | 0.81215 | 268.8 | 77 | 24.8 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 10:15 | PSEL | FLI Proline |  |  |  |  | 7.358 | 39.402 | 38.4 | 1.84 | 35.349 | 153.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3699_5_5_01172020_80.tiff | ./EL/3699_5_5_01172020_20.tiff | ./IV/3699_5_5_01162020.csv | 0 | 0 | 2 | ./RefIV/3699_5_5_01162020.csv | 8.862 | 9.0256 | 2017-01-08 | 8:07 | 1.0099 | 0.99937
515 | 3680 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 1281 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.141 | 37.94 | 8.675 | 0.94902 | 30.52 | 0.80443 | 264.7 | 76.3 | 24.7 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 15:22 | PSEL | FLI Proline |  |  |  |  | 7.338 | 39.252 | 38.4 | 1.835 | 34.974 | 3072 |  |  |  |  | 2.36 | 2021-02-02 |  | 2021-02-02 |  | PSEL | ./EL/3680_5_5_02022021_80.tiff | ./EL/3680_5_5_02022021_20.tiff | ./IV/3680_5_5_02012021.csv | 0 | 1 | 2 | ./RefIV/3680_5_5_02012021.csv | 8.862 | 9.0256 | 7/31/2017 | 11:27 | 1.0108 | 0.98986
516 | 3680 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 899 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.158 | 38 | 8.704 | 0.95043 | 30.89 | 0.81289 | 268.9 | 77.3 | 25 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 10:21 | PSEL | FLI Proline |  |  |  |  | 7.358 | 39.29 | 38.4 | 1.845 | 35.3 | 153.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3680_5_5_01172020_80.tiff | ./EL/3680_5_5_01172020_20.tiff | ./IV/3680_5_5_01162020.csv | 0 | 0 | 2 | ./RefIV/3680_5_5_01162020.csv | 8.862 | 9.0256 | 7/31/2017 | 11:27 | 1.0123 | 1.0003
517 | 3690 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 1281 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.18 | 37.96 | 8.704 | 0.94815 | 30.67 | 0.80796 | 267 | 76.6 | 25.2 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 15:17 | PSEL | FLI Proline |  |  |  |  | 7.338 | 39.99 | 38.4 | 1.835 | 35.049 | 150.6 |  |  |  |  | 2.36 | 2021-02-02 |  | 2021-02-02 |  | PSEL | ./EL/3690_5_5_02022021_80.tiff | ./EL/3690_5_5_02022021_20.tiff | ./IV/3690_5_5_02012021.csv | 0 | 1 | 2 | ./RefIV/3690_5_5_02012021.csv | 8.862 | 9.0256 | 7/31/2017 | 10:47 | 1.0099 | 0.99421
518 | 3690 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 899 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.2 | 38.06 | 8.722 | 0.94804 | 30.97 | 0.81372 | 270.1 | 77.1 | 24.8 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 10:17 | PSEL | FLI Proline |  |  |  |  | 7.358 | 39.477 | 38.4 | 1.84 | 35.499 | 153.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3690_5_5_01172020_80.tiff | ./EL/3690_5_5_01172020_20.tiff | ./IV/3690_5_5_01162020.csv | 0 | 0 | 2 | ./RefIV/3690_5_5_01162020.csv | 8.862 | 9.0256 | 7/31/2017 | 10:47 | 1.0098 | 1.0013
519 | 3703 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 1281 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.199 | 38.01 | 8.703 | 0.94608 | 30.69 | 0.80742 | 267.1 | 76.4 | 24.8 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 15:26 | PSEL | FLI Proline |  |  |  |  | 7.338 | 39.327 | 38.4 | 1.835 | 35.124 | 153.6 |  |  |  |  | 2.36 | 2021-02-02 |  | 2021-02-02 |  | PSEL | ./EL/3703_5_5_02022021_80.tiff | ./EL/3703_5_5_02022021_20.tiff | ./IV/3703_5_5_02012021.csv | 0 | 1 | 2 | ./RefIV/3703_5_5_02012021.csv | 8.862 | 9.0256 | 7/31/2017 | 15:06 | 1.0077 | 0.99354
520 | 3703 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 899 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.21 | 38.05 | 8.714 | 0.94615 | 30.8 | 0.80946 | 268.4 | 76.6 | 25 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 10:09 | PSEL | FLI Proline |  |  |  |  | 7.358 | 39.59 | 38.4 | 1.84 | 35.462 | 153.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3703_5_5_01172020_80.tiff | ./EL/3703_5_5_01172020_20.tiff | ./IV/3703_5_5_01162020.csv | 0 | 0 | 2 | ./RefIV/3703_5_5_01162020.csv | 8.862 | 9.0256 | 7/31/2017 | 15:06 | 1.0078 | 0.99606
521 | 3684 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 1281 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.157 | 37.88 | 8.665 | 0.94627 | 30.59 | 0.80755 | 265 | 76.4 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 15:20 | PSEL | FLI Proline |  |  |  |  | 7.338 | 39.102 | 38.4 | 1.835 | 34.936 | 312.6 |  |  |  |  | 2.36 | 2021-02-02 |  | 2021-02-02 |  | PSEL | ./EL/3684_5_5_02022021_80.tiff | ./EL/3684_5_5_02022021_20.tiff | ./IV/3684_5_5_02012021.csv | 0 | 0 | 1 | ./RefIV/3684_5_5_02012021.csv | 8.862 | 9.0256 | 7/31/2017 | 11:11 | 1.0079 | 0.99371
522 | 3693 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 1280 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.166 | 37.97 | 8.691 | 0.94818 | 30.67 | 0.80774 | 266.5 | 76.6 | 24.7 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 15:25 | PSEL | FLI Proline |  |  |  |  | 7.338 | 39.327 | 38.4 | 1.835 | 35.161 | 153.6 |  |  |  |  | 2.36 | 2021-02-02 |  | 2021-02-02 |  | PSEL | ./EL/3693_5_5_02022021_80.tiff | ./EL/3693_5_5_02022021_20.tiff | ./IV/3693_5_5_02012021.csv | 0 | 1 | 2 | ./RefIV/3693_5_5_02012021.csv | 8.862 | 9.0256 | 2017-01-08 | 8:27 | 1.0099 | 0.99394
523 | 3693 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 898 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.169 | 38.02 | 8.706 | 0.9495 | 30.87 | 0.81194 | 268.8 | 77.1 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 10:11 | PSEL | FLI Proline |  |  |  |  | 7.363 | 39.44 | 38.4 | 1.845 | 35.424 | 153.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3693_5_5_01172020_80.tiff | ./EL/3693_5_5_01172020_20.tiff | ./IV/3693_5_5_01162020.csv | 0 | 0 | 2 | ./RefIV/3693_5_5_01162020.csv | 8.862 | 9.0256 | 2017-01-08 | 8:27 | 1.0114 | 0.99911
524 | 3696 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 1280 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.144 | 37.93 | 8.689 | 0.95024 | 30.6 | 0.80675 | 265.8 | 76.6 | 24.7 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 15:26 | PSEL | FLI Proline |  |  |  |  | 7.338 | 39.065 | 38.4 | 1.835 | 34.974 | 153.6 |  |  |  |  | 2.36 | 2021-02-02 |  | 2021-02-02 |  | PSEL | ./EL/3696_5_5_02022021_80.tiff | ./EL/3696_5_5_02022021_20.tiff | ./IV/3696_5_5_02012021.csv | 0 | 1 | 2 | ./RefIV/3696_5_5_02012021.csv | 8.862 | 9.0256 | 2017-01-08 | 8:19 | 1.0121 | 0.99272
525 | 3696 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 898 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.147 | 37.98 | 8.71 | 0.95222 | 30.92 | 0.81411 | 269.3 | 77.5 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 10:13 | PSEL | FLI Proline |  |  |  |  | 7.358 | 39.327 | 38.4 | 1.845 | 35.349 | 153.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3696_5_5_01172020_80.tiff | ./EL/3696_5_5_01172020_20.tiff | ./IV/3696_5_5_01162020.csv | 0 | 0 | 2 | ./RefIV/3696_5_5_01162020.csv | 8.862 | 9.0256 | 2017-01-08 | 8:19 | 1.0143 | 1.0018
526 | 3247 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 1293 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.18 | 37.93 | 8.693 | 0.94695 | 30.58 | 0.80622 | 265.9 | 76.4 | 25.1 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 15:18 | PSEL | FLI Proline |  |  |  |  | 7.338 | 39.177 | 38.4 | 1.835 | 39.049 | 150.6 |  |  |  |  | 2.36 | 2021-02-02 |  | 2021-02-02 |  | PSEL | ./EL/3247_5_5_02022021_80.tiff | ./EL/3247_5_5_02022021_20.tiff | ./IV/3247_5_5_02012021.csv | 0 | 1 | 2 | ./RefIV/3247_5_5_02012021.csv | 8.862 | 9.0256 | 7/19/2017 | 9:03 | 1.0086 | 0.99207
527 | 3247 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 911 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.188 | 38.01 | 8.719 | 0.94896 | 30.93 | 0.81373 | 269.7 | 77.2 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 10:19 | PSEL | FLI Proline |  |  |  |  | 7.358 | 39.327 | 38.4 | 1.845 | 35.274 | 153.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3247_5_5_01172020_80.tiff | ./EL/3247_5_5_01172020_20.tiff | ./IV/3247_5_5_01162020.csv | 0 | 0 | 2 | ./RefIV/3247_5_5_01162020.csv | 8.862 | 9.0256 | 7/19/2017 | 9:03 | 1.0108 | 1.0013
528 | 3705 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 1281 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.136 | 37.9 | 8.667 | 0.94866 | 30.67 | 0.80923 | 265.8 | 76.8 | 24.6 | back of panel |  | SPIRE | 4600SLP | 2021-01-02 | 15:30 | PSEL | FLI Proline |  |  |  |  | 7.338 | 39.027 | 38.4 | 1.835 | 34.899 | 153.6 |  |  |  |  | 2.36 | 2021-02-02 |  | 2021-02-02 |  | PSEL | ./EL/3705_5_5_02022021_80.tiff | ./EL/3705_5_5_02022021_20.tiff | ./IV/3705_5_5_02012021.csv | 0 | 0 | 1 | ./RefIV/3705_5_5_02012021.csv | 8.862 | 9.0256 | 7/31/2017 | 14:59 | 1.0105 | 0.99578
529 | 3765 |  | 5 | 6 |  | 16335 |  | mono-Si module |  |  | OE 1274 days | 9.31 | 38.3 | 8.8 | 0.94522 | 31.3 | 0.81723 | 275 | 9.341 | 38.54 | 8.897 | 0.95247 | 31.78 | 0.8246 | 282.8 | 78.6 | 24.7 | back of panel |  | SPIRE | 4600SLP | 1/27/2021 | 14:15 | PSEL | FLI Proline |  |  |  |  | 7.498 | 39.515 | 25.6 | 1.875 | 35.799 | 102.6 |  |  |  |  | 2.36 | 1/28/2021 |  | 1/28/2021 |  | PSEL | ./EL/3765_5_6_01282021_80.tiff | ./EL/3765_5_6_01282021_20.tiff | ./IV/3765_5_6_01272021.csv | 0 | 1 | 2 | ./RefIV/3765_5_6_01272021.csv | 8.862 | 9.0256 | 2017-02-08 | 8:41 | 1.0077 | 1.009
530 | 3765 |  | 5 | 6 |  | 16335 |  | mono-Si module |  |  | OE 897 days | 9.31 | 38.3 | 8.8 | 0.94522 | 31.3 | 0.81723 | 275 | 9.349 | 38.53 | 8.904 | 0.9524 | 31.77 | 0.82455 | 282.9 | 78.5 | 24.7 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 9:11 | PSEL | FLI Proline |  |  |  |  | 7.508 | 39.853 | 25.6 | 1.88 | 36.137 | 102.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3765_5_6_01172020_80.tiff | ./EL/3765_5_6_01172020_20.tiff | ./IV/3765_5_6_01162020.csv | 0 | 0 | 2 | ./RefIV/3765_5_6_01162020.csv | 8.862 | 9.0256 | 2017-02-08 | 8:41 | 1.0076 | 1.009
531 | 3646 |  | 5 | 6 |  | 16335 |  | mono-Si module |  |  | OE 1280 days | 9.31 | 38.3 | 8.8 | 0.94522 | 31.3 | 0.81723 | 275 | 9.415 | 38.49 | 8.929 | 0.94838 | 31.47 | 0.81761 | 281 | 77.5 | 24.7 | back of panel |  | SPIRE | 4600SLP | 1/27/2021 | 14:33 | PSEL | FLI Proline |  |  |  |  | 7.498 | 39.74 | 25.6 | 1.875 | 35.762 | 102.6 |  |  |  |  | 2.36 | 1/28/2021 |  | 1/28/2021 |  | PSEL | ./EL/3646_5_6_01282021_80.tiff | ./EL/3646_5_6_01282021_20.tiff | ./IV/3646_5_6_01272021.csv | 0 | 1 | 2 | ./RefIV/3646_5_6_01272021.csv | 8.862 | 9.0256 | 7/27/2017 | 11:37 | 1.0033 | 1.0005
532 | 3646 |  | 5 | 6 |  | 16335 |  | mono-Si module |  |  | OE 903 days | 9.31 | 38.3 | 8.8 | 0.94522 | 31.3 | 0.81723 | 275 | 9.425 | 38.48 | 8.933 | 0.9478 | 31.52 | 0.81913 | 281.6 | 77.6 | 24.8 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 9:25 | PSEL | FLI Proline |  |  |  |  | 7.508 | 40.003 | 25.6 | 1.825 | 36.062 | 102.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3646_5_6_01172020_80.tiff | ./EL/3646_5_6_01172020_20.tiff | ./IV/3646_5_6_01162020.csv | 0 | 0 | 2 | ./RefIV/3646_5_6_01162020.csv | 8.862 | 9.0256 | 7/27/2017 | 11:37 | 1.0027 | 1.0023
533 | 3657 |  | 5 | 6 |  | 16335 |  | mono-Si module |  |  | OE 1280 days | 9.31 | 38.3 | 8.8 | 0.94522 | 31.3 | 0.81723 | 275 | 9.381 | 38.49 | 8.936 | 0.95256 | 31.37 | 0.81502 | 280.3 | 77.6 | 24.6 | back of panel |  | SPIRE | 4600SLP | 1/27/2021 | 14:31 | PSEL | FLI Proline |  |  |  |  | 7.498 | 39.965 | 25.6 | 1.875 | 35.874 | 102.6 |  |  |  |  | 2.36 | 1/28/2021 |  | 1/28/2021 |  | PSEL | ./EL/3657_5_6_01282021_80.tiff | ./EL/3657_5_6_01282021_20.tiff | ./IV/3657_5_6_01272021.csv | 0 | 1 | 2 | ./RefIV/3657_5_6_01272021.csv | 8.862 | 9.0256 | 7/27/2017 | 11:04 | 1.0078 | 0.99729
534 | 3657 |  | 5 | 6 |  | 16335 |  | mono-Si module |  |  | OE 903 days | 9.31 | 38.3 | 8.8 | 0.94522 | 31.3 | 0.81723 | 275 | 9.393 | 38.49 | 8.946 | 0.95241 | 31.45 | 0.8171 | 281.4 | 77.8 | 24.8 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 9:27 | PSEL | FLI Proline |  |  |  |  | 7.513 | 39.978 | 25.6 | 1.88 | 36.025 | 102.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3657_5_6_01172020_80.tiff | ./EL/3657_5_6_01172020_20.tiff | ./IV/3657_5_6_01162020.csv | 0 | 0 | 2 | ./RefIV/3657_5_6_01162020.csv | 8.862 | 9.0256 | 7/27/2017 | 11:04 | 1.0076 | 0.99983
535 | 3257 |  | 5 | 6 |  | 16335 |  | mono-Si module |  |  | OE 1288 days | 9.31 | 38.3 | 8.8 | 0.94522 | 31.3 | 0.81723 | 275 | 9.325 | 38.45 | 8.893 | 0.95367 | 31.54 | 0.82029 | 280.5 | 78.2 | 24.7 | back of panel |  | SPIRE | 4600SLP | 1/27/2021 | 14:23 | PSEL | FLI Proline |  |  |  |  | 7.498 | 39.628 | 25.6 | 1.875 | 36.612 | 102.6 |  |  |  |  | 2.36 | 1/28/2021 |  | 1/28/2021 |  | PSEL | ./EL/3257_5_6_01282021_80.tiff | ./EL/3257_5_6_01282021_20.tiff | ./IV/3257_5_6_01272021.csv | 0 | 0 | 1 | ./RefIV/3257_5_6_01272021.csv | 8.862 | 9.0256 | 7/19/2017 | 10:08 | 1.0089 | 1.0037
536 | 3255 |  | 5 | 6 |  | 16335 |  | mono-Si module |  |  | OE 1288 days | 9.31 | 38.3 | 8.8 | 0.94522 | 31.3 | 0.81723 | 275 | 9.381 | 38.23 | 8.896 | 0.9483 | 31.09 | 0.81324 | 276.6 | 77.1 | 24.6 | back of panel |  | SPIRE | 4600SLP | 1/27/2021 | 13:38 | PSEL | FLI Proline |  |  |  |  | 7.498 | 39.356 | 25.6 | 1.875 | 35.124 | 102.6 |  |  |  |  | 2.36 | 1/28/2021 |  | 1/28/2021 |  | PSEL | ./EL/3255_5_6_01282021_80.tiff | ./EL/3255_5_6_01282021_20.tiff | ./IV/3255_5_6_01272021.csv | 0 | 1 | 3 | ./RefIV/3255_5_6_01272021.csv | 8.862 | 9.0256 | 7/19/2017 | 9:59 | 1.0033 | 0.99511
537 | 3255 |  | 5 | 6 |  | 16335 |  | mono-Si module |  |  | OE 911 days | 9.31 | 38.3 | 8.8 | 0.94522 | 31.3 | 0.81723 | 275 | 9.378 | 38.2 | 8.888 | 0.94775 | 31.09 | 0.81387 | 276.3 | 77.1 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 9:05 | PSEL | FLI Proline |  |  |  |  | 7.513 | 39.59 | 25.6 | 1.88 | 35.618 | 102.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3255_5_6_01172020_80.tiff | ./EL/3255_5_6_01172020_20.tiff | ./IV/3255_5_6_01162020.csv | 0 | 0 | 3 | ./RefIV/3255_5_6_01162020.csv | 8.862 | 9.0256 | 7/19/2017 | 9:59 | 1.0027 | 0.99589
538 | 3255 |  | 5 | 6 |  | 16335 |  | mono-Si module |  |  | OE 5 days | 9.31 | 38.3 | 8.8 | 0.94522 | 31.3 | 0.81723 | 275 | 9.553 | 38.03 | 9.049 | 0.94724 | 30.89 | 0.81225 | 279.5 | 76.9 | 25.7 | back of panel |  | SPIRE | 4600SLP | 7/24/2017 | 8:47 | PSEL | FLI Proline |  |  |  |  | 7.458 | 38.952 | 38.4 | 1.865 | 34.936 | 153.6 |  |  |  |  | 2.36 | 7/26/2017 |  | 7/26/2017 |  | PSEL | ./EL/3255_5_6_07262017_80.tiff | ./EL/3255_5_6_07262017_20.tiff | ./IV/3255_5_6_07242017.csv | 0 | 2 | 3 | ./RefIV/3255_5_6_07242017.csv | 9.0256 | 9.0256 | 7/19/2017 | 9:59 | 1.0021 | 0.99391
539 | 3256 |  | 5 | 6 |  | 16335 |  | mono-Si module |  |  | OE 1288 days | 9.31 | 38.3 | 8.8 | 0.94522 | 31.3 | 0.81723 | 275 | 9.352 | 38.28 | 8.921 | 0.95391 | 31.23 | 0.81583 | 278.6 | 77.8 | 24.6 | back of panel |  | SPIRE | 4600SLP | 1/27/2021 | 13:42 | PSEL | FLI Proline |  |  |  |  | 7.498 | 39.023 | 25.6 | 1.87 | 34.936 | 102.6 |  |  |  |  | 2.36 | 1/28/2021 |  | 1/28/2021 |  | PSEL | ./EL/3256_5_6_01282021_80.tiff | ./EL/3256_5_6_01282021_20.tiff | ./IV/3256_5_6_01272021.csv | 0 | 1 | 3 | ./RefIV/3256_5_6_01272021.csv | 8.862 | 9.0256 | 7/19/2017 | 10:05 | 1.0092 | 0.99828
540 | 3256 |  | 5 | 6 |  | 16335 |  | mono-Si module |  |  | OE 911 days | 9.31 | 38.3 | 8.8 | 0.94522 | 31.3 | 0.81723 | 275 | 9.35 | 38.2 | 8.912 | 0.95316 | 31.18 | 0.81623 | 277.9 | 77.8 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 9:02 | PSEL | FLI Proline |  |  |  |  | 7.508 | 39.44 | 25.6 | 1.88 | 35.537 | 102.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3256_5_6_01172020_80.tiff | ./EL/3256_5_6_01172020_20.tiff | ./IV/3256_5_6_01162020.csv | 0 | 0 | 3 | ./RefIV/3256_5_6_01162020.csv | 8.862 | 9.0256 | 7/19/2017 | 10:05 | 1.0084 | 0.99877
541 | 3256 |  | 5 | 6 |  | 16335 |  | mono-Si module |  |  | OE 5 days | 9.31 | 38.3 | 8.8 | 0.94522 | 31.3 | 0.81723 | 275 | 9.519 | 38.09 | 9.065 | 0.95231 | 31.03 | 0.81465 | 281.3 | 77.6 | 25.5 | back of panel |  | SPIRE | 4600SLP | 7/24/2017 | 8:50 | PSEL | FLI Proline |  |  |  |  | 7.458 | 38.802 | 25.6 | 1.865 | 34.936 | 153.6 |  |  |  |  | 2.36 | 7/26/2017 |  | 7/26/2017 |  | PSEL | ./EL/3256_5_6_07262017_80.tiff | ./EL/3256_5_6_07262017_20.tiff | ./IV/3256_5_6_07242017.csv | 0 | 2 | 3 | ./RefIV/3256_5_6_07242017.csv | 9.0256 | 9.0256 | 7/19/2017 | 10:05 | 1.0075 | 0.99684
542 | 3770 |  | 5 | 6 |  | 16335 |  | mono-Si module |  |  | OE 1274 days | 9.31 | 38.3 | 8.8 | 0.94522 | 31.3 | 0.81723 | 275 | 9.37 | 38.64 | 8.946 | 0.95475 | 31.81 | 0.82324 | 284.5 | 78.6 | 24.8 | back of panel |  | SPIRE | 4600SLP | 1/27/2021 | 14:20 | PSEL | FLI Proline |  |  |  |  | 7.498 | 39.74 | 25.6 | 1.875 | 35..95 | 102.6 |  |  |  |  | 2.36 | 1/28/2021 |  | 1/28/2021 |  | PSEL | ./EL/3770_5_6_01282021_80.tiff | ./EL/3770_5_6_01282021_20.tiff | ./IV/3770_5_6_01272021.csv | 0 | 0 | 1 | ./RefIV/3770_5_6_01272021.csv | 8.862 | 9.0256 | 2017-02-08 | 8:21 | 1.0101 | 1.0074
543 | 3666 |  | 5 | 6 |  | 16335 |  | mono-Si module |  |  | OE 1280 days | 9.31 | 38.3 | 8.8 | 0.94522 | 31.3 | 0.81723 | 275 | 9.302 | 38.52 | 8.865 | 0.95302 | 31.56 | 0.81931 | 279.7 | 78.1 | 24.7 | back of panel |  | SPIRE | 4600SLP | 1/27/2021 | 14:25 | PSEL | FLI Proline |  |  |  |  | 7.498 | 39.74 | 25.6 | 1.875 | 35.784 | 102.6 |  |  |  |  | 2.36 | 1/28/2021 |  | 1/28/2021 |  | PSEL | ./EL/3666_5_6_01282021_80.tiff | ./EL/3666_5_6_01282021_20.tiff | ./IV/3666_5_6_01272021.csv | 0 | 1 | 2 | ./RefIV/3666_5_6_01272021.csv | 8.862 | 9.0256 | 7/27/2017 | 10:33 | 1.0083 | 1.0025
544 | 3666 |  | 5 | 6 |  | 16335 |  | mono-Si module |  |  | OE 903 days | 9.31 | 38.3 | 8.8 | 0.94522 | 31.3 | 0.81723 | 275 | 9.311 | 38.51 | 8.867 | 0.95231 | 31.59 | 0.82031 | 280.1 | 78.1 | 24.8 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 9:32 | PSEL | FLI Proline |  |  |  |  | 7.508 | 39.928 | 25.6 | 1.88 | 36.062 | 102.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3666_5_6_01172020_80.tiff | ./EL/3666_5_6_01172020_20.tiff | ./IV/3666_5_6_01162020.csv | 0 | 0 | 2 | ./RefIV/3666_5_6_01162020.csv | 8.862 | 9.0256 | 7/27/2017 | 10:33 | 1.0075 | 1.0038
545 | 3648 |  | 5 | 6 |  | 16335 |  | mono-Si module |  |  | OE 1280 days | 9.31 | 38.3 | 8.8 | 0.94522 | 31.3 | 0.81723 | 275 | 9.365 | 38.52 | 8.896 | 0.94992 | 31.54 | 0.8188 | 280.6 | 77.8 | 24.8 | back of panel |  | SPIRE | 4600SLP | 1/27/2021 | 14:34 | PSEL | FLI Proline |  |  |  |  | 7.498 | 39.74 | 25.6 | 1.875 | 35.874 | 102.6 |  |  |  |  | 2.36 | 1/28/2021 |  | 1/28/2021 |  | PSEL | ./EL/3648_5_6_01282021_80.tiff | ./EL/3648_5_6_01282021_20.tiff | ./IV/3648_5_6_01272021.csv | 0 | 0 | 1 | ./RefIV/3648_5_6_01272021.csv | 8.862 | 9.0256 | 7/27/2017 | 11:31 | 1.005 | 1.0019
546 | 3659 |  | 5 | 6 |  | 16335 |  | mono-Si module |  |  | OE 1280 days | 9.31 | 38.3 | 8.8 | 0.94522 | 31.3 | 0.81723 | 275 | 9.378 | 38.53 | 8.937 | 0.95298 | 31.58 | 0.81962 | 282.3 | 78.1 | 24.8 | back of panel |  | SPIRE | 4600SLP | 1/27/2021 | 14:27 | PSEL | FLI Proline |  |  |  |  | 7.498 | 39.74 | 25.6 | 1.87 | 35.844 | 102.6 |  |  |  |  | 2.36 | 1/28/2021 |  | 1/28/2021 |  | PSEL | ./EL/3659_5_6_01282021_80.tiff | ./EL/3659_5_6_01282021_20.tiff | ./IV/3659_5_6_01272021.csv | 0 | 1 | 2 | ./RefIV/3659_5_6_01272021.csv | 8.862 | 9.0256 | 7/27/2017 | 10:58 | 1.0082 | 1.0029
547 | 3659 |  | 5 | 6 |  | 16335 |  | mono-Si module |  |  | OE 903 days | 9.31 | 38.3 | 8.8 | 0.94522 | 31.3 | 0.81723 | 275 | 9.394 | 38.52 | 8.942 | 0.95188 | 31.58 | 0.81983 | 282.4 | 78.1 | 24.7 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 9:30 | PSEL | FLI Proline |  |  |  |  | 7.518 | 39.853 | 25.6 | 1.88 | 36.025 | 102.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3659_5_6_01172020_80.tiff | ./EL/3659_5_6_01172020_20.tiff | ./IV/3659_5_6_01162020.csv | 0 | 0 | 2 | ./RefIV/3659_5_6_01162020.csv | 8.862 | 9.0256 | 7/27/2017 | 10:58 | 1.0071 | 1.0032
548 | 3763 |  | 5 | 6 |  | 16335 |  | mono-Si module |  |  | OE 1274 days | 9.31 | 38.3 | 8.8 | 0.94522 | 31.3 | 0.81723 | 275 | 9.357 | 38.62 | 8.936 | 0.95501 | 31.84 | 0.82444 | 284.5 | 78.7 | 24.6 | back of panel |  | SPIRE | 4600SLP | 1/27/2021 | 14:17 | PSEL | FLI Proline |  |  |  |  | 7.498 | 39.703 | 25.6 | 1.87 | 35.95 | 102.6 |  |  |  |  | 2.36 | 1/28/2021 |  | 1/28/2021 |  | PSEL | ./EL/3763_5_6_01282021_80.tiff | ./EL/3763_5_6_01282021_20.tiff | ./IV/3763_5_6_01272021.csv | 0 | 1 | 2 | ./RefIV/3763_5_6_01272021.csv | 8.862 | 9.0256 | 2017-02-08 | 8:49 | 1.0104 | 1.0088
549 | 3763 |  | 5 | 6 |  | 16335 |  | mono-Si module |  |  | OE 897 days | 9.31 | 38.3 | 8.8 | 0.94522 | 31.3 | 0.81723 | 275 | 9.361 | 38.6 | 8.941 | 0.95513 | 31.83 | 0.82461 | 284.6 | 78.8 | 24.8 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 9:13 | PSEL | FLI Proline |  |  |  |  | 7.508 | 39.965 | 25.6 | 1.875 | 36.25 | 102.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3763_5_6_01172020_80.tiff | ./EL/3763_5_6_01172020_20.tiff | ./IV/3763_5_6_01162020.csv | 0 | 0 | 2 | ./RefIV/3763_5_6_01162020.csv | 8.862 | 9.0256 | 2017-02-08 | 8:49 | 1.0105 | 1.009
550 | 3652 |  | 5 | 6 |  | 16335 |  | mono-Si module |  |  | OE 1280 days | 9.31 | 38.3 | 8.8 | 0.94522 | 31.3 | 0.81723 | 275 | 9.402 | 38.51 | 8.955 | 0.95246 | 31.6 | 0.82057 | 283 | 78.2 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/27/2021 | 14:10 | PSEL | FLI Proline |  |  |  |  | 7.498 | 39.665 | 25.6 | 1.875 | 35.837 | 102.6 |  |  |  |  | 2.36 | 1/28/2021 |  | 1/28/2021 |  | PSEL | ./EL/3652_5_6_01282021_80.tiff | ./EL/3652_5_6_01282021_20.tiff | ./IV/3652_5_6_01272021.csv | 0 | 1 | 2 | ./RefIV/3652_5_6_01272021.csv | 8.862 | 9.0256 | 7/27/2017 | 11:21 | 1.0077 | 1.0041
551 | 3652 |  | 5 | 6 |  | 16335 |  | mono-Si module |  |  | OE 903 days | 9.31 | 38.3 | 8.8 | 0.94522 | 31.3 | 0.81723 | 275 | 9.413 | 38.53 | 8.962 | 0.95209 | 31.63 | 0.82092 | 283.5 | 78.2 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 9:20 | PSEL | FLI Proline |  |  |  |  | 7.508 | 39.065 | 25.6 | 1.88 | 35.612 | 102.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3652_5_6_01172020_80.tiff | ./EL/3652_5_6_01172020_20.tiff | ./IV/3652_5_6_01162020.csv | 0 | 0 | 2 | ./RefIV/3652_5_6_01162020.csv | 8.862 | 9.0256 | 7/27/2017 | 11:21 | 1.0073 | 1.0045
552 | 3759 |  | 5 | 6 |  | 16335 |  | mono-Si module |  |  | OE 1274 days | 9.31 | 38.3 | 8.8 | 0.94522 | 31.3 | 0.81723 | 275 | 9.352 | 38.62 | 8.926 | 0.95445 | 31.79 | 0.82315 | 283.7 | 78.6 | 24.7 | back of panel |  | SPIRE | 4600SLP | 1/27/2021 | 14:19 | PSEL | FLI Proline |  |  |  |  | 7.493 | 39.628 | 25.6 | 1.87 | 35.874 | 102.6 |  |  |  |  | 2.36 | 1/28/2021 |  | 1/28/2021 |  | PSEL | ./EL/3759_5_6_01282021_80.tiff | ./EL/3759_5_6_01282021_20.tiff | ./IV/3759_5_6_01272021.csv | 0 | 1 | 2 | ./RefIV/3759_5_6_01272021.csv | 8.862 | 9.0256 | 2017-02-08 | 9:05 | 1.0098 | 1.0072
553 | 3759 |  | 5 | 6 |  | 16335 |  | mono-Si module |  |  | OE 897 days | 9.31 | 38.3 | 8.8 | 0.94522 | 31.3 | 0.81723 | 275 | 9.36 | 38.59 | 8.931 | 0.95417 | 31.79 | 0.82379 | 284 | 78.6 | 24.8 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 9:17 | PSEL | FLI Proline |  |  |  |  | 7.508 | 39.74 | 25.6 | 1.88 | 36.1 | 102.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3759_5_6_01172020_80.tiff | ./EL/3759_5_6_01172020_20.tiff | ./IV/3759_5_6_01162020.csv | 0 | 0 | 2 | ./RefIV/3759_5_6_01162020.csv | 8.862 | 9.0256 | 2017-02-08 | 9:05 | 1.0095 | 1.008
554 | 3779 |  | 5 | 6 |  | 16335 |  | mono-Si module |  |  | OE 1274 days | 9.31 | 38.3 | 8.8 | 0.94522 | 31.3 | 0.81723 | 275 | 9.339 | 38.54 | 8.914 | 0.95449 | 31.78 | 0.8246 | 283.2 | 78.7 | 24.7 | back of panel |  | SPIRE | 4600SLP | 1/27/2021 | 14:22 | PSEL | FLI Proline |  |  |  |  | 7.498 | 39.59 | 25.6 | 1.87 | 35.874 | 102.6 |  |  |  |  | 2.36 | 1/28/2021 |  | 1/28/2021 |  | PSEL | ./EL/3779_5_6_01282021_80.tiff | ./EL/3779_5_6_01282021_20.tiff | ./IV/3779_5_6_01272021.csv | 0 | 1 | 2 | ./RefIV/3779_5_6_01272021.csv | 8.862 | 9.0256 | 2017-02-08 | 7:50 | 1.0098 | 1.009
555 | 3779 |  | 5 | 6 |  | 16335 |  | mono-Si module |  |  | OE 897 days | 9.31 | 38.3 | 8.8 | 0.94522 | 31.3 | 0.81723 | 275 | 9.345 | 38.52 | 8.912 | 0.95367 | 31.78 | 0.82503 | 283.2 | 78.7 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 9:19 | PSEL | FLI Proline |  |  |  |  | 7.508 | 39.74 | 25.6 | 1.885 | 36.1 | 102.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3779_5_6_01172020_80.tiff | ./EL/3779_5_6_01172020_20.tiff | ./IV/3779_5_6_01162020.csv | 0 | 0 | 2 | ./RefIV/3779_5_6_01162020.csv | 8.862 | 9.0256 | 2017-02-08 | 7:50 | 1.0089 | 1.0095
556 | 3647 |  | 5 | 6 |  | 16335 |  | mono-Si module |  |  | OE 1280 days | 9.31 | 38.3 | 8.8 | 0.94522 | 31.3 | 0.81723 | 275 | 9.364 | 38.47 | 8.927 | 0.95333 | 31.51 | 0.81908 | 281.3 | 78.1 | 24.8 | back of panel |  | SPIRE | 4600SLP | 1/27/2021 | 14:36 | PSEL | FLI Proline |  |  |  |  | 7.508 | 39.703 | 25.6 | 1.87 | 35.724 | 102.6 |  |  |  |  | 2.36 | 1/28/2021 |  | 1/28/2021 |  | PSEL | ./EL/3647_5_6_01282021_80.tiff | ./EL/3647_5_6_01282021_20.tiff | ./IV/3647_5_6_01272021.csv | 0 | 1 | 2 | ./RefIV/3647_5_6_01272021.csv | 8.862 | 9.0256 | 7/27/2017 | 11:34 | 1.0086 | 1.0023
557 | 3647 |  | 5 | 6 |  | 16335 |  | mono-Si module |  |  | OE 903 days | 9.31 | 38.3 | 8.8 | 0.94522 | 31.3 | 0.81723 | 275 | 9.386 | 38.48 | 8.938 | 0.95227 | 31.54 | 0.81965 | 281.9 | 78 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 9:24 | PSEL | FLI Proline |  |  |  |  | 7.503 | 39.978 | 25.6 | 1.88 | 35.912 | 102.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3647_5_6_01172020_80.tiff | ./EL/3647_5_6_01172020_20.tiff | ./IV/3647_5_6_01162020.csv | 0 | 0 | 2 | ./RefIV/3647_5_6_01162020.csv | 8.862 | 9.0256 | 7/27/2017 | 11:34 | 1.0075 | 1.003
558 | 3769 |  | 5 | 6 |  | 16335 |  | mono-Si module |  |  | OE 1274 days | 9.31 | 38.3 | 8.8 | 0.94522 | 31.3 | 0.81723 | 275 | 9.343 | 38.59 | 8.941 | 0.95697 | 31.83 | 0.82483 | 284.6 | 78.9 | 24.7 | back of panel |  | SPIRE | 4600SLP | 1/27/2021 | 14:13 | PSEL | FLI Proline |  |  |  |  | 7.498 | 39.74 | 25.6 | 1.875 | 35.874 | 102.6 |  |  |  |  | 2.36 | 1/28/2021 |  | 1/28/2021 |  | PSEL | ./EL/3769_5_6_01282021_80.tiff | ./EL/3769_5_6_01282021_20.tiff | ./IV/3769_5_6_01272021.csv | 0 | 1 | 2 | ./RefIV/3769_5_6_01272021.csv | 8.862 | 9.0256 | 2017-02-08 | 8:26 | 1.0124 | 1.0093
559 | 3769 |  | 5 | 6 |  | 16335 |  | mono-Si module |  |  | OE 897 days | 9.31 | 38.3 | 8.8 | 0.94522 | 31.3 | 0.81723 | 275 | 9.352 | 38.65 | 8.944 | 0.95637 | 31.91 | 0.82561 | 285.4 | 79 | 24.7 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 9:09 | PSEL | FLI Proline |  |  |  |  | 7.508 | 39.965 | 25.6 | 1.88 | 36.212 | 102.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3769_5_6_01172020_80.tiff | ./EL/3769_5_6_01172020_20.tiff | ./IV/3769_5_6_01162020.csv | 0 | 0 | 2 | ./RefIV/3769_5_6_01162020.csv | 8.862 | 9.0256 | 2017-02-08 | 8:26 | 1.0118 | 1.0103
560 | 3687 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 899 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.159 | 38.06 | 8.709 | 0.95087 | 31.05 | 0.81582 | 270.4 | 77.6 | 24.7 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 10:28 | PSEL | FLI Proline |  |  |  |  | 7.358 | 39.29 | 38.4 | 1.845 | 35.311 | 153.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3687_5_5_01172020_80.tiff | ./EL/3687_5_5_01172020_20.tiff | ./IV/3687_5_5_01162020.csv | 0 | 0 | 1 | ./RefIV/3687_5_5_01162020.csv | 8.862 | 9.0256 | 7/31/2017 | 11:00 | 1.0128 | 1.0039
561 | 3650 |  | 5 | 6 |  | 16335 |  | mono-Si module |  |  | OE 903 days | 9.31 | 38.3 | 8.8 | 0.94522 | 31.3 | 0.81723 | 275 | 9.434 | 38.5 | 8.958 | 0.94954 | 31.54 | 0.81922 | 282.6 | 77.8 | 24.8 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 9:22 | PSEL | FLI Proline |  |  |  |  | 7.508 | 39.908 | 25.6 | 1.88 | 35.912 | 102.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3650_5_6_01172020_80.tiff | ./EL/3650_5_6_01172020_20.tiff | ./IV/3650_5_6_01162020.csv | 0 | 0 | 1 | ./RefIV/3650_5_6_01162020.csv | 8.862 | 9.0256 | 7/27/2017 | 11:26 | 1.0046 | 1.0024
562 | 3676 |  | 5 | 5 |  | 16394.4 |  | multi-Si module |  |  | OE 899 days | 9.32 | 37.9 | 8.75 | 0.93884 | 30.8 | 0.81266 | 270 | 9.15 | 38.05 | 8.707 | 0.95158 | 30.97 | 0.81393 | 269.7 | 77.4 | 24.7 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 10:24 | PSEL | FLI Proline |  |  |  |  | 7.363 | 39.065 | 38.4 | 1.845 | 35.124 | 153.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3676_5_5_01172020_80.tiff | ./EL/3676_5_5_01172020_20.tiff | ./IV/3676_5_5_01162020.csv | 0 | 0 | 1 | ./RefIV/3676_5_5_01162020.csv | 8.862 | 9.0256 | 7/31/2017 | 11:48 | 1.0136 | 1.0016
563 | 3762 |  | 5 | 6 |  | 16335 |  | mono-Si module |  |  | OE 897 days | 9.31 | 38.3 | 8.8 | 0.94522 | 31.3 | 0.81723 | 275 | 9.367 | 38.56 | 8.945 | 0.95495 | 31.83 | 0.82547 | 284.7 | 78.8 | 24.9 | back of panel |  | SPIRE | 4600SLP | 1/16/2020 | 9:15 | PSEL | FLI Proline |  |  |  |  | 7.513 | 39.965 | 25.6 | 1.88 | 36.287 | 102.6 |  |  |  |  | 2.36 | 1/17/2020 |  | 1/17/2020 |  | PSEL | ./EL/3762_5_6_01172020_80.tiff | ./EL/3762_5_6_01172020_20.tiff | ./IV/3762_5_6_01162020.csv | 0 | 0 | 1 | ./RefIV/3762_5_6_01162020.csv | 8.862 | 9.0256 | 2017-02-08 | 8:54 | 1.0103 | 1.0101
564 | 2436 |  | 36 | 1 |  | 12425.2 |  | mono-Si module |  |  | OE 0 days | 5.99 | 48.7 | 5.61 | 0.93656 | 41 | 0.84189 | 230 | 6.072 | 48.79 | 5.672 | 0.93412 | 40.73 | 0.8348 | 231 | 78 | 25.1 | back of panel |  | SPIRE | 4600SLP | 3/27/2019 | 18:25 | PSEL | FLI Proline |  |  |  |  | 4.866 | 49.573 | 6.4 | 1.216 | 45.993 | 19.2 |  |  |  |  | 1.8 | 3/20/2019 |  | 3/20/2019 |  | PSEL | ./EL/2436_36_1_03202019_80.tiff | ./EL/2436_36_1_03202019_20.tiff | ./IV/2436_36_1_03272019.csv | 0 | 0 | 1 | ./RefIV/2436_36_1_03272019.csv | 8.862 | 8.862 | 3/27/2019 | 18:25 | 0.9974 | 0.99158
565 | 2438 |  | 36 | 1 |  | 12425.2 |  | mono-Si module |  |  | OE 0 days | 5.99 | 48.7 | 5.61 | 0.93656 | 41 | 0.84189 | 230 | 5.898 | 48.56 | 5.483 | 0.92964 | 40.46 | 0.8332 | 221.9 | 77.5 | 25.3 | back of panel |  | SPIRE | 4600SLP | 3/27/2019 | 18:41 | PSEL | FLI Proline |  |  |  |  | 4.727 | 49.799 | 6.45 | 1.181 | 45.708 | 19.2 |  |  |  |  | 1.8 | 3/20/2019 |  | 3/20/2019 |  | PSEL | ./EL/2438_36_1_03202019_80.tiff | ./EL/2438_36_1_03202019_20.tiff | ./IV/2438_36_1_03272019.csv | 0 | 0 | 1 | ./RefIV/2438_36_1_03272019.csv | 8.862 | 8.862 | 3/27/2019 | 18:41 | 0.99261 | 0.98967
566 | 2530 |  | 36 | 1 |  | 12425.2 |  | mono-Si module |  |  | OE 0 days | 5.99 | 48.7 | 5.61 | 0.93656 | 41 | 0.84189 | 230 | 5.914 | 48.33 | 5.5 | 0.93 | 40.26 | 0.83302 | 221.5 | 77.5 | 25 | back of panel |  | SPIRE | 4600SLP | 2019-05-08 | 8:02 | PSEL | FLI Proline |  |  |  |  | 4.737 | 49.573 | 6.4 | 1.181 | 45.445 | 25.6 |  |  |  |  | 2.36 | 2019-06-08 |  | 2019-06-08 |  | PSEL | ./EL/2530_36_1_08062019_80.tiff | ./EL/2530_36_1_08062019_20.tiff | ./IV/2530_36_1_08052019.csv | 0 | 0 | 1 | ./RefIV/2530_36_1_08052019.csv | 8.862 | 8.862 | 2019-05-08 | 8:02 | 0.99299 | 0.98947
567 | 2531 |  | 36 | 1 |  | 12425.2 |  | mono-Si module |  |  | OE 0 days | 5.99 | 48.7 | 5.61 | 0.93656 | 41 | 0.84189 | 230 | 5.994 | 48.45 | 5.557 | 0.92709 | 40.18 | 0.82931 | 223.2 | 76.9 | 24.9 | back of panel |  | SPIRE | 4600SLP | 2019-05-08 | 8:05 | PSEL | FLI Proline |  |  |  |  | 4.801 | 49.724 | 6.4 | 1.201 | 45.67 | 25.6 |  |  |  |  | 2.36 | 2019-06-08 |  | 2019-06-08 |  | PSEL | ./EL/2531_36_1_08062019_80.tiff | ./EL/2531_36_1_08062019_20.tiff | ./IV/2531_36_1_08052019.csv | 0 | 0 | 1 | ./RefIV/2531_36_1_08052019.csv | 8.862 | 8.862 | 2019-05-08 | 8:05 | 0.98989 | 0.98506
568 | 2541 |  | 36 | 1 |  | 12425.2 |  | mono-Si module |  |  | OE 0 days | 5.99 | 48.7 | 5.61 | 0.93656 | 41 | 0.84189 | 230 | 6.05 | 48.46 | 5.659 | 0.93537 | 40.33 | 0.83223 | 228.2 | 77.8 | 25.1 | back of panel |  | SPIRE | 4600SLP | 3/27/2019 | 18:54 | PSEL | FLI Proline |  |  |  |  | 4.864 | 49.686 | 6.4 | 1.21 | 45.633 | 19.2 |  |  |  |  | 1.8 | 3/20/2019 |  | 3/20/2019 |  | PSEL | ./EL/2541_36_1_03202019_80.tiff | ./EL/2541_36_1_03202019_20.tiff | ./IV/2541_36_1_03272019.csv | 0 | 0 | 1 | ./RefIV/2541_36_1_03272019.csv | 8.862 | 8.862 | 3/27/2019 | 18:54 | 0.99873 | 0.98853
569 | 2440 |  | 36 | 1 |  | 12425.2 |  | mono-Si module |  |  | OE 0 days | 5.99 | 48.7 | 5.61 | 0.93656 | 41 | 0.84189 | 230 | 6.06 | 48.75 | 5.672 | 0.93597 | 40.67 | 0.83426 | 230.7 | 78.1 | 25.4 | back of panel |  | SPIRE | 4600SLP | 3/27/2019 | 18:49 | PSEL | FLI Proline |  |  |  |  | 4.856 | 50.024 | 6.4 | 1.211 | 45.97 | 19.2 |  |  |  |  | 1.8 | 3/20/2019 |  | 3/20/2019 |  | PSEL | ./EL/2440_36_1_03202019_80.tiff | ./EL/2440_36_1_03202019_20.tiff | ./IV/2440_36_1_03272019.csv | 0 | 0 | 1 | ./RefIV/2440_36_1_03272019.csv | 8.862 | 8.862 | 3/27/2019 | 18:49 | 0.99937 | 0.99093
570 | 2533 |  | 36 | 1 |  | 12425.2 |  | mono-Si module |  |  | OE 0 days | 5.99 | 48.7 | 5.61 | 0.93656 | 41 | 0.84189 | 230 | 6.07 | 48.84 | 5.654 | 0.93147 | 40.61 | 0.83149 | 229.6 | 77.5 | 25 | back of panel |  | SPIRE | 4600SLP | 2019-05-08 | 8:10 | PSEL | FLI Proline |  |  |  |  | 4.861 | 50.136 | 6.4 | 1.166 | 45.899 | 25.6 |  |  |  |  | 2.36 | 2019-06-08 |  | 2019-06-08 |  | PSEL | ./EL/2533_36_1_08062019_80.tiff | ./EL/2533_36_1_08062019_20.tiff | ./IV/2533_36_1_08052019.csv | 0 | 0 | 1 | ./RefIV/2533_36_1_08052019.csv | 8.862 | 8.862 | 2019-05-08 | 8:10 | 0.99456 | 0.98765
571 | 2529 |  | 36 | 1 |  | 12425.2 |  | mono-Si module |  |  | OE 0 days | 5.99 | 48.7 | 5.61 | 0.93656 | 41 | 0.84189 | 230 | 5.908 | 48.38 | 5.556 | 0.94042 | 40.29 | 0.83278 | 223.8 | 78.3 | 25.3 | back of panel |  | SPIRE | 4600SLP | 2019-05-08 | 7:58 | PSEL | FLI Proline |  |  |  |  | 4.73 | 49.048 | 6.4 | 1.18 | 45.02 | 25.6 |  |  |  |  | 2.36 | 2019-06-08 |  | 2019-06-08 |  | PSEL | ./EL/2529_36_1_08062019_80.tiff | ./EL/2529_36_1_08062019_20.tiff | ./IV/2529_36_1_08052019.csv | 0 | 0 | 1 | ./RefIV/2529_36_1_08052019.csv | 8.862 | 8.862 | 2019-05-08 | 7:58 | 1.0041 | 0.98918
572 | 2532 |  | 36 | 1 |  | 12425.2 |  | mono-Si module |  |  | OE 0 days | 5.99 | 48.7 | 5.61 | 0.93656 | 41 | 0.84189 | 230 | 6.056 | 48.88 | 5.671 | 0.93643 | 40.85 | 0.83572 | 231.7 | 78.2 | 25 | back of panel |  | SPIRE | 4600SLP | 2019-05-08 | 8:08 | PSEL | FLI Proline |  |  |  |  | 4.846 | 50.174 | 6.4 | 1.216 | 45.196 | 25.6 |  |  |  |  | 2.36 | 2019-06-08 |  | 2019-06-08 |  | PSEL | ./EL/2532_36_1_08062019_80.tiff | ./EL/2532_36_1_08062019_20.tiff | ./IV/2532_36_1_08052019.csv | 0 | 0 | 1 | ./RefIV/2532_36_1_08052019.csv | 8.862 | 8.862 | 2019-05-08 | 8:08 | 0.99986 | 0.99267
573 | 3501 |  | 24 | 2 |  | 16671.6 |  | mono-Si module |  |  | OE 21 days | 11.4 | 39.2 | 10.8 | 0.94737 | 31.7 | 0.80867 | 270 | 8.9321 | 38.9816 | 8.4507 | 0.94611 | 31.6313 | 0.81144 | 267.306 | 76.771 | 25 | back of panel |  | SPIRE | 4600SLP | 8/17/2016 | 10:47 | PSEL | FLI Proline |  |  |  |  | 8.002 | 40.266 | 19.2 | 1.995 | 36.25 | 76.8 |  |  |  |  | 2.6 | 8/17/2016 |  | 8/17/2016 |  | PSEL | ./EL/3501_24_2_08172016_80.tiff | ./EL/3501_24_2_08172016_20.tiff | ./IV/3501_24_2_08172016.csv | 0 | 1 | 2 | ./RefIV/3501_24_2_08172016.csv |  |  | 7/27/2016 | 12:20 | 0.99867 | 1.0034
574 | 3395 |  | 30 | 1 |  | 16416.9 |  | multi-Si module |  |  | OE 0 days |  |  |  | #DIV/0! |  | #DIV/0! |  | 8.6989 | 42.8023 | 8.197 | 0.9423 | 34.3984 | 0.80366 | 281.963 | 75.728 | 25 | back of panel |  | SPIRE | 4600SLP | 3/18/2016 | 13:56 | PSEL | FLI Proline |  |  |  |  | 6.809 | 44.919 | 1.6 | 1.7 | 40.228 | 9.6 | [5 empty] | 3/18/2016 |  | 3/18/2016 |  | PSEL | ./EL/3395_30_1_03182016_80.tiff | ./EL/3395_30_1_03182016_20.tiff | ./IV/3395_30_1_03182016.csv | 0 | 0 | 1 | ./RefIV/3395_30_1_03182016.csv |  |  | 3/18/2016 | 13:53 | #DIV/0! | #DIV/0!
575 | 3394 |  | 30 | 1 |  | 16416.9 |  | multi-Si module |  |  | OE 0 days |  |  |  | #DIV/0! |  | #DIV/0! |  | 8.6756 | 42.7916 | 8.1848 | 0.94343 | 34.1942 | 0.79909 | 279.874 | 75.387 | 25 | back of panel |  | SPIRE | 4600SLP | 3/18/2016 | 12:54 | PSEL | FLI Proline |  |  |  |  | 6.809 | 44.844 | 1.6 | 1.7 | 39.965 | 9.6 | [5 empty] | 3/18/2016 |  | 3/18/2016 |  | PSEL | ./EL/3394_30_1_03182016_80.tiff | ./EL/3394_30_1_03182016_20.tiff | ./IV/3394_30_1_03182016.csv | 0 | 0 | 1 | ./RefIV/3394_30_1_03182016.csv |  |  | 3/18/2016 | 12:51 | #DIV/0! | #DIV/0!
576 | 3411 |  | 30 | 1 |  | 16416.9 |  | multi-Si module |  |  | OE 0 days |  |  |  | #DIV/0! |  | #DIV/0! |  | 8.6855 | 42.752 | 8.1829 | 0.94213 | 34.293 | 0.80214 | 280.616 | 75.572 | 25 | back of panel |  | SPIRE | 4600SLP | 3/18/2016 | 14:35 | PSEL | FLI Proline |  |  |  |  | 6.809 | 44.844 | 1.6 | 1.7 | 40.115 | 9.6 | [5 empty] | 3/18/2016 |  | 3/18/2016 |  | PSEL | ./EL/3411_30_1_03182016_80.tiff | ./EL/3411_30_1_03182016_20.tiff | ./IV/3411_30_1_03182016.csv | 0 | 0 | 1 | ./RefIV/3411_30_1_03182016.csv |  |  | 3/18/2016 | 14:32 | #DIV/0! | #DIV/0!
577 | 3396 |  | 30 | 1 |  | 16416.9 |  | multi-Si module |  |  | OE 0 days |  |  |  | #DIV/0! |  | #DIV/0! |  | 8.5803 | 42.5301 | 8.0935 | 0.94327 | 34.0752 | 0.8012 | 275.789 | 75.575 | 25 | back of panel |  | SPIRE | 4600SLP | 2016-04-04 | 14:38 | PSEL | FLI Proline |  |  |  |  | 6.804 | 44.019 | 1.6 | 1.7 | 39.327 | 9.6 | [5 empty] | 2016-04-04 |  | 2016-04-04 |  | PSEL | ./EL/3396_30_1_04042016_80.tiff | ./EL/3396_30_1_04042016_20.tiff | ./IV/3396_30_1_04042016.csv | 0 | 0 | 1 | ./RefIV/3396_30_1_04042016.csv |  |  | 2016-04-04 | 14:36 | #DIV/0! | #DIV/0!
578 | 3199 |  | 30 | 4 |  | 16252.4 |  | multi-Si module |  |  | OE 0 days |  |  |  | #DIV/0! |  | #DIV/0! |  | 8.8024 | 42.6932 | 8.217 | 0.9335 | 34.3258 | 0.80401 | 282.056 | 75.054 | 25 | back of panel |  | SPIRE | 4600SLP | 12/15/2015 | 16:32 | PSEL | FLI Proline |  |  |  |  | 8.85 | 46.15 | 1.2 | 2.21 | 41.24 | 6.4 | [5 empty] | 12/16/2015 |  | 12/16/2015 |  | PSEL | ./EL/3199_30_4_12162015_80.tiff | ./EL/3199_30_4_12162015_20.tiff | ./IV/3199_30_4_12152015.csv | 0 | 0 | 1 | ./RefIV/3199_30_4_12152015.csv |  |  | 12/15/2015 | 16:32 | #DIV/0! | #DIV/0!
579 | 3197 |  | 30 | 4 |  | 16252.4 |  | multi-Si module |  |  | OE 0 days |  |  |  | #DIV/0! |  | #DIV/0! |  | 8.7841 | 42.6491 | 8.2281 | 0.9367 | 34.215 | 0.80224 | 281.523 | 75.146 | 25 | back of panel |  | SPIRE | 4600SLP | 12/15/2015 | 16:18 | PSEL | FLI Proline |  |  |  |  | 8.901 | 46.16 | 1.2 | 2.21 | 41.24 | 6.4 | [5 empty] | 12/16/2015 |  | 12/16/2015 |  | PSEL | ./EL/3197_30_4_12162015_80.tiff | ./EL/3197_30_4_12162015_20.tiff | ./IV/3197_30_4_12152015.csv | 0 | 0 | 1 | ./RefIV/3197_30_4_12152015.csv |  |  | 12/15/2015 | 16:18 | #DIV/0! | #DIV/0!
580 | 3201 |  | 30 | 4 |  | 16252.4 |  | multi-Si module |  |  | OE 0 days |  |  |  | #DIV/0! |  | #DIV/0! |  | 8.7217 | 42.5295 | 8.2119 | 0.94155 | 33.9846 | 0.79908 | 279.078 | 75.237 | 25 | back of panel |  | SPIRE | 4600SLP | 12/15/2015 | 16:41 | PSEL | FLI Proline |  |  |  |  | 8.86 | 45.75 | 1.25 | 2.21 | 40.83 | 6.4 | [5 empty] | 12/16/2015 |  | 12/16/2015 |  | PSEL | ./EL/3201_30_4_12162015_80.tiff | ./EL/3201_30_4_12162015_20.tiff | ./IV/3201_30_4_12152015.csv | 0 | 0 | 1 | ./RefIV/3201_30_4_12152015.csv |  |  | 12/15/2015 | 16:41 | #DIV/0! | #DIV/0!
581 | 3160 |  | 30 | 4 |  | 16252.4 |  | multi-Si module |  |  | OE 0 days |  |  |  | #DIV/0! |  | #DIV/0! |  | 8.7392 | 42.6115 | 8.22 | 0.94058 | 34.0885 | 0.79998 | 280.206 | 75.245 | 25 | back of panel |  | SPIRE | 4600SLP | 12/21/2015 | 15:10 | PSEL | FLI Proline |  |  |  |  | 8.86 | 46 | 1.25 | 2.23 | 41.05 | 6.4 | [5 empty] | 12/22/2015 |  | 12/22/2015 |  | PSEL | ./EL/3160_30_4_12222015_80.tiff | ./EL/3160_30_4_12222015_20.tiff | ./IV/3160_30_4_12212015.csv | 0 | 0 | 1 | ./RefIV/3160_30_4_12212015.csv |  |  | 12/21/2015 | 15:10 | #DIV/0! | #DIV/0!
582 | 3159 |  | 30 | 4 |  | 16252.4 |  | multi-Si module |  |  | OE 0 days |  |  |  | #DIV/0! |  | #DIV/0! |  | 8.762 | 42.6235 | 8.2385 | 0.94025 | 34.059 | 0.79907 | 280.594 | 75.132 | 25 | back of panel |  | SPIRE | 4600SLP | 12/21/2015 | 15:03 | PSEL | FLI Proline |  |  |  |  | 8.936 | 45.93 | 1.25 | 2.23 | 41.05 | 6.4 | [5 empty] | 12/22/2015 |  | 12/22/2015 |  | PSEL | ./EL/3159_30_4_12222015_80.tiff | ./EL/3159_30_4_12222015_20.tiff | ./IV/3159_30_4_12212015.csv | 0 | 0 | 1 | ./RefIV/3159_30_4_12212015.csv |  |  | 12/21/2015 | 15:03 | #DIV/0! | #DIV/0!
583 | 3195 |  | 30 | 4 |  | 16252.4 |  | multi-Si module |  |  | OE 0 days |  |  |  | #DIV/0! |  | #DIV/0! |  | 8.7077 | 42.5598 | 8.2108 | 0.94293 | 34.0987 | 0.8012 | 279.978 | 75.547 | 25 | back of panel |  | SPIRE | 4600SLP | 12/15/2015 | 16:02 | PSEL | FLI Proline |  |  |  |  | 8.89 | 46.04 | 1.25 | 2.21 | 41.05 | 6.4 | [5 empty] | 12/16/2015 |  | 12/16/2015 |  | PSEL | ./EL/3195_30_4_12162015_80.tiff | ./EL/3195_30_4_12162015_20.tiff | ./IV/3195_30_4_12152015.csv | 0 | 0 | 1 | ./RefIV/3195_30_4_12152015.csv |  |  | 12/15/2015 | 16:02 | #DIV/0! | #DIV/0!
584 | 3188 |  | 38 | 2 |  | 16368 |  | multi-Si module |  |  | OE 0 days | 8.62 | 37.7 | 8.12 | 0.942 | 31.4 | 0.83289 | 255 | 8.9055 | 38.0223 | 8.4328 | 0.94691 | 30.8151 | 0.81045 | 259.856 | 76.742 | 25 | back of panel |  | SPIRE | 4600SLP | 12/15/2015 | 15:15 | PSEL | FLI Proline |  |  |  |  | 8.936 | 40.528 | 38.4 | 2.23 | 36.55 | 153.6 | [5 empty] | 12/16/2015 |  | 12/16/2015 |  | PSEL | ./EL/3188_38_2_12162015_80.tiff | ./EL/3188_38_2_12162015_20.tiff | ./IV/3188_38_2_12152015.csv | 0 | 0 | 1 | ./RefIV/3188_38_2_12152015.csv |  |  | 12/15/2015 | 15:15 | 1.0052 | 0.97305
585 | 3189 |  | 38 | 2 |  | 16368 |  | multi-Si module |  |  | OE 0 days | 8.62 | 37.7 | 8.12 | 0.942 | 31.4 | 0.83289 | 255 | 8.8688 | 37.821 | 8.4134 | 0.94866 | 30.7856 | 0.81398 | 259.011 | 77.218 | 25 | back of panel |  | SPIRE | 4600SLP | 12/15/2015 | 15:20 | PSEL | FLI Proline |  |  |  |  | 8.936 | 40.303 | 38.4 | 2.23 | 36.3 | 153.6 | [5 empty] | 12/16/2015 |  | 12/16/2015 |  | PSEL | ./EL/3189_38_2_12162015_80.tiff | ./EL/3189_38_2_12162015_20.tiff | ./IV/3189_38_2_12152015.csv | 0 | 0 | 1 | ./RefIV/3189_38_2_12152015.csv |  |  | 12/15/2015 | 15:20 | 1.0071 | 0.9773
586 | 3186 |  | 38 | 2 |  | 16368 |  | multi-Si module |  |  | OE 0 days | 8.62 | 37.7 | 8.12 | 0.942 | 31.4 | 0.83289 | 255 | 8.8477 | 37.8462 | 8.382 | 0.94736 | 30.8199 | 0.81435 | 258.331 | 77.147 | 25 | back of panel |  | SPIRE | 4600SLP | 12/15/2015 | 14:34 | PSEL | FLI Proline |  |  |  |  | 8.936 | 40.641 | 38.4 | 2.23 | 36.475 | 153.6 | [5 empty] | 12/16/2015 |  | 12/16/2015 |  | PSEL | ./EL/3186_38_2_12162015_80.tiff | ./EL/3186_38_2_12162015_20.tiff | ./IV/3186_38_2_12152015.csv | 0 | 0 | 1 | ./RefIV/3186_38_2_12152015.csv |  |  | 12/15/2015 | 14:34 | 1.0057 | 0.97773
587 | 3187 |  | 38 | 2 |  | 16368 |  | multi-Si module |  |  | OE 0 days | 8.62 | 37.7 | 8.12 | 0.942 | 31.4 | 0.83289 | 255 | 8.8423 | 37.8467 | 8.4337 | 0.9538 | 30.7655 | 0.8129 | 259.469 | 77.534 | 25 | back of panel |  | SPIRE | 4600SLP | 12/15/2015 | 14:50 | PSEL | FLI Proline |  |  |  |  | 8.936 | 40.603 | 38.4 | 2.23 | 36.43 | 153.6 | [5 empty] | 12/16/2015 |  | 12/16/2015 |  | PSEL | ./EL/3187_38_2_12162015_80.tiff | ./EL/3187_38_2_12162015_20.tiff | ./IV/3187_38_2_12152015.csv | 0 | 0 | 1 | ./RefIV/3187_38_2_12152015.csv |  |  | 12/15/2015 | 14:50 | 1.0125 | 0.976
588 | 3191 |  | 38 | 2 |  | 16368 |  | multi-Si module |  |  | OE 0 days | 8.62 | 37.7 | 8.12 | 0.942 | 31.4 | 0.83289 | 255 | 8.8576 | 37.9252 | 8.418 | 0.95036 | 30.9123 | 0.81509 | 260.218 | 77.462 | 25 | back of panel |  | SPIRE | 4600SLP | 12/15/2015 | 15:31 | PSEL | FLI Proline |  |  |  |  | 8.936 | 39.93 | 38.4 | 2.23 | 35.61 | 153.6 | [5 empty] | 12/16/2015 |  | 12/16/2015 |  | PSEL | ./EL/3191_38_2_12162015_80.tiff | ./EL/3191_38_2_12162015_20.tiff | ./IV/3191_38_2_12152015.csv | 0 | 0 | 1 | ./RefIV/3191_38_2_12152015.csv |  |  | 12/15/2015 | 15:31 | 1.0089 | 0.97862
589 | 3161 |  | 38 | 2 |  | 16368 |  | multi-Si module |  |  | OE 0 days | 8.62 | 37.7 | 8.12 | 0.942 | 31.4 | 0.83289 | 255 | 8.8942 | 37.8997 | 8.4341 | 0.94826 | 30.7322 | 0.81088 | 259.198 | 76.893 | 25 | back of panel |  | SPIRE | 4600SLP | 12/21/2015 | 15:33 | PSEL | FLI Proline |  |  |  |  | 8.936 | 40.38 | 38.4 | 2.23 | 36.13 | 153.6 | [5 empty] | 12/22/2015 |  | 12/22/2015 |  | PSEL | ./EL/3161_38_2_12222015_80.tiff | ./EL/3161_38_2_12222015_20.tiff | ./IV/3161_38_2_12212015.csv | 0 | 0 | 1 | ./RefIV/3161_38_2_12212015.csv |  |  | 12/21/2015 | 15:33 | 1.0067 | 0.97358
590 | 3240 |  | 38 | 2 |  | 16368 |  | multi-Si module |  |  | OE 0 days | 8.62 | 37.7 | 8.12 | 0.942 | 31.4 | 0.83289 | 255 | 8.885 | 37.8927 | 8.4612 | 0.9523 | 30.7451 | 0.81137 | 260.141 | 77.266 | 25 | back of panel |  | SPIRE | 4600SLP | 12/21/2015 | 15:28 | PSEL | FLI Proline |  |  |  |  | 8.936 | 40.38 | 38.4 | 2.23 | 36.4 | 153.6 | [5 empty] | 12/22/2015 |  | 12/22/2015 |  | PSEL | ./EL/3240_38_2_12222015_80.tiff | ./EL/3240_38_2_12222015_20.tiff | ./IV/3240_38_2_12212015.csv | 0 | 0 | 1 | ./RefIV/3240_38_2_12212015.csv |  |  | 12/21/2015 | 15:28 | 1.0109 | 0.97416
591 | 3185 |  | 38 | 2 |  | 16368 |  | multi-Si module |  |  | OE 0 days | 8.62 | 37.7 | 8.12 | 0.942 | 31.4 | 0.83289 | 255 | 8.9147 | 37.8743 | 8.4492 | 0.94778 | 30.8713 | 0.8151 | 260.839 | 77.253 | 25 | back of panel |  | SPIRE | 4600SLP | 12/15/2015 | 14:21 | PSEL | FLI Proline |  |  |  |  | 8.936 | 40.378 | 38.4 | 2.23 | 36.475 | 153.6 | [5 empty] | 12/16/2015 |  | 12/16/2015 |  | PSEL | ./EL/3185_38_2_12162015_80.tiff | ./EL/3185_38_2_12162015_20.tiff | ./IV/3185_38_2_12152015.csv | 0 | 0 | 1 | ./RefIV/3185_38_2_12152015.csv |  |  | 12/15/2015 | 14:21 | 1.0061 | 0.97864
592 | 3190 |  | 38 | 2 |  | 16368 |  | multi-Si module |  |  | OE 0 days | 8.62 | 37.7 | 8.12 | 0.942 | 31.4 | 0.83289 | 255 | 8.9006 | 37.9672 | 8.4284 | 0.94696 | 30.9934 | 0.81632 | 261.226 | 77.302 | 25 | back of panel |  | SPIRE | 4600SLP | 12/15/2015 | 15:26 | PSEL | FLI Proline |  |  |  |  | 8.93 | 40.42 | 38.4 | 2.23 | 36.475 | 153.6 | [5 empty] | 12/16/2015 |  | 12/16/2015 |  | PSEL | ./EL/3190_38_2_12162015_80.tiff | ./EL/3190_38_2_12162015_20.tiff | ./IV/3190_38_2_12152015.csv | 0 | 0 | 1 | ./RefIV/3190_38_2_12152015.csv |  |  | 12/15/2015 | 15:26 | 1.0053 | 0.9801
593 | 3353 |  | 34 | 8 |  | 16766.7 |  | multi-Si module |  |  | OE 0 days | 8.94 | 39.7 | 8.37 | 0.93624 | 31.4 | 0.79093 | 260 | 8.9331 | 36.9924 | 8.4715 | 0.94833 | 29.3211 | 0.79262 | 248.395 | 75.167 | 25 | back of panel |  | SPIRE | 4600SLP | 3/15/2016 | 12:43 | PSEL | FLI Proline |  |  |  |  | 7.104 | 38.99 | 51.2 | 1.7 | 34.768 | 307.2 | [5 empty] | 3/15/2016 |  | 3/15/2016 |  | PSEL | ./EL/3353_34_8_03152016_80.tiff | ./EL/3353_34_8_03152016_20.tiff | ./IV/3353_34_8_03152016.csv | 0 | 0 | 1 | ./RefIV/3353_34_8_03152016.csv |  |  | 3/15/2016 | 12:43 | 1.0129 | 1.0021
594 | 3340 |  | 34 | 8 |  | 16766.7 |  | multi-Si module |  |  | OE 0 days | 8.94 | 39.7 | 8.37 | 0.93624 | 31.4 | 0.79093 | 260 | 8.9195 | 37.4042 | 8.4888 | 0.95171 | 30.1504 | 0.80607 | 255.941 | 76.714 | 25 | back of panel |  | SPIRE | 4600SLP | 3/14/2016 | 15:13 | PSEL | FLI Proline |  |  |  |  | 7.109 | 38.839 | 51.2 | 1.785 | 34.824 | 307.2 | [5 empty] | 3/14/2016 |  | 3/14/2016 |  | PSEL | ./EL/3340_34_8_03142016_80.tiff | ./EL/3340_34_8_03142016_20.tiff | ./IV/3340_34_8_03142016.csv | 0 | 0 | 1 | ./RefIV/3340_34_8_03142016.csv |  |  | 3/14/2016 | 15:13 | 1.0165 | 1.0191
595 | 3346 |  | 34 | 8 |  | 16766.7 |  | multi-Si module |  |  | OE 0 days | 8.94 | 39.7 | 8.37 | 0.93624 | 31.4 | 0.79093 | 260 | 8.9412 | 37.4852 | 8.4642 | 0.94665 | 30.3627 | 0.80999 | 256.997 | 76.678 | 25 | back of panel |  | SPIRE | 4600SLP | 3/15/2016 | 9:01 | PSEL | FLI Proline | [7 empty] | 1.7 | 34.561 | 307.2 | [7 empty] | 3/14/2016 |  | PSEL |  | ./EL/3346_34_8_03142016_20.tiff | ./IV/3346_34_8_03152016.csv | 0 | 0 | 2 | ./RefIV/3346_34_8_03152016.csv |  |  | 3/15/2016 | 9:01 | 1.0111 | 1.0241
596 | 3346 |  | 34 | 8 |  | 16766.7 |  | multi-Si module |  |  | OE 0 days | 8.94 | 39.7 | 8.37 | 0.93624 | 31.4 | 0.79093 | 260 | 8.9412 | 37.4852 | 8.4642 | 0.94665 | 30.3627 | 0.80999 | 256.997 | 76.678 | 25 | back of panel |  | SPIRE | 4600SLP | 3/15/2016 | 9:01 | PSEL | FLI Proline |  |  |  |  | 7.104 | 38.577 | 51.2 | 1.7 | 34.561 | 307.2 | [5 empty] | 3/15/2016 |  | 3/15/2016 |  | PSEL | ./EL/3346_34_8_03152016_80.tiff | ./EL/3346_34_8_03152016_20.tiff | ./IV/3346_34_8_03152016.csv | 0 | 1 | 2 | ./RefIV/3346_34_8_03152016.csv |  |  | 3/15/2016 | 9:01 | 1.0111 | 1.0241
597 | 3387 |  | 34 | 4 |  | 16766.7 |  | multi-Si module |  |  | OE 0 days | 9.44 | 39.2 | 8.81 | 0.93326 | 30.9 | 0.78827 | 270 | 9.0008 | 38.7257 | 8.5728 | 0.95245 | 31.0216 | 0.80106 | 265.942 | 76.296 | 25 | back of panel |  | SPIRE | 4600SLP | 3/17/2016 | 15:30 | PSEL | FLI Proline |  |  |  |  | 7.508 | 40.941 | 12.8 | 1.8 | 36.55 | 76.8 | [5 empty] | 3/17/2016 |  | 3/17/2016 |  | PSEL | ./EL/3387_34_4_03172016_80.tiff | ./EL/3387_34_4_03172016_20.tiff | ./IV/3387_34_4_03172016.csv | 0 | 0 | 1 | ./RefIV/3387_34_4_03172016.csv |  |  | 3/17/2016 | 15:30 | 1.0206 | 1.0162
598 | 3382 |  | 34 | 4 |  | 16766.7 |  | multi-Si module |  |  | OE 0 days | 9.44 | 39.2 | 8.81 | 0.93326 | 30.9 | 0.78827 | 270 | 8.9853 | 38.7072 | 8.5411 | 0.95056 | 31.0645 | 0.80255 | 265.325 | 76.287 | 25 | back of panel |  | SPIRE | 4600SLP | 3/17/2016 | 13:39 | PSEL | FLI Proline |  |  |  |  | 7.508 | 41.091 | 19.2 | 1.805 | 36.512 | 76.8 | [5 empty] | 3/17/2016 |  | 3/17/2016 |  | PSEL | ./EL/3382_34_4_03172016_80.tiff | ./EL/3382_34_4_03172016_20.tiff | ./IV/3382_34_4_03172016.csv | 0 | 0 | 1 | ./RefIV/3382_34_4_03172016.csv |  |  | 3/17/2016 | 13:39 | 1.0185 | 1.0181
599 | 3383 |  | 34 | 4 |  | 16766.7 |  | multi-Si module |  |  | OE 0 days | 9.44 | 39.2 | 8.81 | 0.93326 | 30.9 | 0.78827 | 270 | 8.9362 | 38.6985 | 8.5217 | 0.95361 | 31.1827 | 0.80579 | 265.729 | 76.84 | 25 | back of panel |  | SPIRE | 4600SLP | 3/17/2016 | 14:15 | PSEL | FLI Proline |  |  |  |  | 7.503 | 40.866 | 12.8 | 1.805 | 36.437 | 76.8 | [5 empty] | 3/17/2016 |  | 3/17/2016 |  | PSEL | ./EL/3383_34_4_03172016_80.tiff | ./EL/3383_34_4_03172016_20.tiff | ./IV/3383_34_4_03172016.csv | 0 | 0 | 1 | ./RefIV/3383_34_4_03172016.csv |  |  | 3/17/2016 | 14:15 | 1.0218 | 1.0222
600 | 3381 |  | 34 | 4 |  | 16766.7 |  | multi-Si module |  |  | OE 0 days | 9.44 | 39.2 | 8.81 | 0.93326 | 30.9 | 0.78827 | 270 | 8.9757 | 38.7699 | 8.5038 | 0.94743 | 31.133 | 0.80302 | 264.751 | 76.08 | 25 | back of panel |  | SPIRE | 4600SLP | 3/17/2016 | 13:15 | PSEL | FLI Proline |  |  |  |  | 7.503 | 42.214 | 19.2 | 1.705 | 36.7 | 76.8 | [5 empty] | 3/17/2016 |  | 3/17/2016 |  | PSEL | ./EL/3381_34_4_03172016_80.tiff | ./EL/3381_34_4_03172016_20.tiff | ./IV/3381_34_4_03172016.csv | 0 | 0 | 1 | ./RefIV/3381_34_4_03172016.csv |  |  | 3/17/2016 | 13:15 | 1.0152 | 1.0187
601 | 3384 |  | 34 | 4 |  | 16766.7 |  | multi-Si module |  |  | OE 0 days | 9.44 | 39.2 | 8.81 | 0.93326 | 30.9 | 0.78827 | 270 | 8.97 | 38.7529 | 8.6128 | 0.96019 | 30.8833 | 0.79693 | 265.992 | 76.519 | 25 | back of panel |  | SPIRE | 4600SLP | 3/17/2016 | 14:34 | PSEL | FLI Proline |  |  |  |  | 7.508 | 41.241 | 12.8 | 1.805 | 36.663 | 76.8 | [5 empty] | 3/17/2016 |  | 3/17/2016 |  | PSEL | ./EL/3384_34_4_03172016_80.tiff | ./EL/3384_34_4_03172016_20.tiff | ./IV/3384_34_4_03172016.csv | 0 | 0 | 1 | ./RefIV/3384_34_4_03172016.csv |  |  | 3/17/2016 | 14:34 | 1.0288 | 1.011
602 | 3388 |  | 34 | 4 |  | 16766.7 |  | multi-Si module |  |  | OE 0 days | 9.44 | 39.2 | 8.81 | 0.93326 | 30.9 | 0.78827 | 270 | 8.9481 | 38.7416 | 8.5337 | 0.95369 | 30.9176 | 0.79805 | 263.841 | 76.108 | 25 | back of panel |  | SPIRE | 4600SLP | 3/17/2016 | 16:15 | PSEL | FLI Proline |  |  |  |  | 7.508 | 41.316 | 12.8 | 1.8 | 36.512 | 76.8 | [5 empty] | 3/17/2016 |  | 3/17/2016 |  | PSEL | ./EL/3388_34_4_03172016_80.tiff | ./EL/3388_34_4_03172016_20.tiff | ./IV/3388_34_4_03172016.csv | 0 | 0 | 1 | ./RefIV/3388_34_4_03172016.csv |  |  | 3/17/2016 | 16:15 | 1.0219 | 1.0124
603 | 3389 |  | 34 | 4 |  | 16766.7 |  | multi-Si module |  |  | OE 0 days | 9.44 | 39.2 | 8.81 | 0.93326 | 30.9 | 0.78827 | 270 | 8.9446 | 38.622 | 8.5823 | 0.9595 | 30.9993 | 0.80263 | 266.047 | 77.012 | 25 | back of panel |  | SPIRE | 4600SLP | 3/17/2016 | 15:59 | PSEL | FLI Proline |  |  |  |  | 7.508 | 40.866 | 19.2 | 1.8 | 36.325 | 76.8 | [5 empty] | 3/17/2016 |  | 3/17/2016 |  | PSEL | ./EL/3389_34_4_03172016_80.tiff | ./EL/3389_34_4_03172016_20.tiff | ./IV/3389_34_4_03172016.csv | 0 | 0 | 1 | ./RefIV/3389_34_4_03172016.csv |  |  | 3/17/2016 | 15:59 | 1.0281 | 1.0182
604 | 3393 |  | 34 | 4 |  | 16766.7 |  | multi-Si module |  |  | OE 0 days | 9.44 | 39.2 | 8.81 | 0.93326 | 30.9 | 0.78827 | 270 | 8.9268 | 38.7841 | 8.5441 | 0.95713 | 31.1239 | 0.80249 | 265.927 | 76.808 | 25 | back of panel |  | SPIRE | 4600SLP | 3/17/2016 | 17:09 | PSEL | FLI Proline |  |  |  |  | 7.508 | 41.166 | 12.8 | 1.8 | 36.598 | 1.28 | [5 empty] | 3/17/2016 |  | 3/17/2016 |  | PSEL | ./EL/3393_34_4_03172016_80.tiff | ./EL/3393_34_4_03172016_20.tiff | ./IV/3393_34_4_03172016.csv | 0 | 0 | 1 | ./RefIV/3393_34_4_03172016.csv |  |  | 3/17/2016 | 17:09 | 1.0256 | 1.018
605 | 3339 |  | 34 | 10 |  | 16766.7 |  | multi-Si module |  |  | OE 0 days | 9.97 | 39.9 | 9.33 | 0.93581 | 31.4 | 0.78697 | 290 | 9.3601 | 38.7289 | 8.9428 | 0.95542 | 31.2064 | 0.80577 | 279.073 | 76.983 | 25 | back of panel |  | SPIRE | 4600SLP | 3/14/2016 | 13:18 | PSEL | FLI Proline |  |  |  |  | 7.508 | 40.528 | 19.2 | 1.805 | 36.212 | 76.8 | [5 empty] | 3/14/2016 |  | 3/14/2016 |  | PSEL | ./EL/3339_34_10_03142016_80.tiff | ./EL/3339_34_10_03142016_20.tiff | ./IV/3339_34_10_03142016.csv | 0 | 0 | 1 | ./RefIV/3339_34_10_03142016.csv |  |  | 3/14/2016 | 13:18 | 1.021 | 1.0239
606 | 3327 |  | 34 | 10 |  | 16766.7 |  | multi-Si module |  |  | OE 0 days | 9.97 | 39.9 | 9.33 | 0.93581 | 31.4 | 0.78697 | 290 | 9.292 | 38.6254 | 8.8839 | 0.95608 | 31.1851 | 0.80737 | 277.045 | 77.191 | 25 | back of panel |  | SPIRE | 4600SLP | 3/14/2016 | 9:57 | PSEL | FLI Proline |  |  |  |  | 7.508 | 39.628 | 19.2 | 1.8 | 35.874 | 76.8 | [5 empty] | 3/14/2016 |  | 3/14/2016 |  | PSEL | ./EL/3327_34_10_03142016_80.tiff | ./EL/3327_34_10_03142016_20.tiff | ./IV/3327_34_10_03142016.csv | 0 | 0 | 1 | ./RefIV/3327_34_10_03142016.csv |  |  | 3/14/2016 | 9:57 | 1.0217 | 1.0259
607 | 3333 |  | 34 | 10 |  | 16766.7 |  | multi-Si module |  |  | OE 0 days | 9.97 | 39.9 | 9.33 | 0.93581 | 31.4 | 0.78697 | 290 | 9.3233 | 38.6998 | 8.9837 | 0.96358 | 30.7416 | 0.79436 | 276.174 | 76.543 | 25 | back of panel |  | SPIRE | 4600SLP | 3/14/2016 | 12:03 | PSEL | FLI Proline |  |  |  |  | 7.508 | 40.528 | 19.2 | 1.805 | 36.212 | 76.8 | [5 empty] | 3/14/2016 |  | 3/14/2016 |  | PSEL | ./EL/3333_34_10_03142016_80.tiff | ./EL/3333_34_10_03142016_20.tiff | ./IV/3333_34_10_03142016.csv | 0 | 0 | 1 | ./RefIV/3333_34_10_03142016.csv |  |  | 3/14/2016 | 12:03 | 1.0297 | 1.0094
608 | 3359 |  | 36 | 4 |  | 21620.8 |  | multi-Si module |  |  | OE 0 days |  |  |  | #DIV/0! |  | #DIV/0! |  | 6.0855 | 92.7007 | 5.6855 | 0.93427 | 78.8777 | 0.85089 | 448.462 | 79.495 | 25 | back of panel |  | SPIRE | 4600SLP | 3/16/2016 | 8:31 | PSEL | FLI Proline |  |  |  |  | 4.811 | 94.423 | 1.2 | 1.206 | 87.893 | 4.8 | [5 empty] | 3/16/2016 |  | 3/16/2016 |  | PSEL | ./EL/3359_36_4_03162016_80.tiff | ./EL/3359_36_4_03162016_20.tiff | ./IV/3359_36_4_03162016.csv | 0 | 0 | 1 | ./RefIV/3359_36_4_03162016.csv |  |  | 3/16/2016 | 8:31 | #DIV/0! | #DIV/0!
609 | 3360 |  | 36 | 4 |  | 21620.8 |  | multi-Si module |  |  | OE 0 days |  |  |  | #DIV/0! |  | #DIV/0! |  | 6.0947 | 92.7297 | 5.6867 | 0.93307 | 79.0461 | 0.85244 | 449.515 | 79.537 | 25 | back of panel |  | SPIRE | 4600SLP | 3/16/2016 | 9:08 | PSEL | FLI Proline |  |  |  |  | 4.806 | 94.436 | 1.2 | 1.206 | 88.118 | 4.8 | [5 empty] | 3/16/2016 |  | 3/16/2016 |  | PSEL | ./EL/3360_36_4_03162016_80.tiff | ./EL/3360_36_4_03162016_20.tiff | ./IV/3360_36_4_03162016.csv | 0 | 0 | 1 | ./RefIV/3360_36_4_03162016.csv |  |  | 3/16/2016 | 9:08 | #DIV/0! | #DIV/0!
610 | 3371 |  | 36 | 7 |  | 21620.8 |  | multi-Si module |  |  | OE 0 days |  |  |  | #DIV/0! |  | #DIV/0! |  | 6.109 | 86.4961 | 5.7901 | 0.9478 | 72.678 | 0.84025 | 420.812 | 79.638 | 25 | back of panel |  | SPIRE | 4600SLP | 3/16/2016 | 13:03 | PSEL | FLI Proline |  |  |  |  | 4.811 | 88.043 | 6.4 | 1.206 | 81.475 | 19.2 | [5 empty] | 3/18/2016 |  | 3/18/2016 |  | PSEL | ./EL/3371_36_7_03182016_80.tiff | ./EL/3371_36_7_03182016_20.tiff | ./IV/3371_36_7_03162016.csv | 0 | 0 | 1 | ./RefIV/3371_36_7_03162016.csv |  |  | 3/16/2016 | 13:00 | #DIV/0! | #DIV/0!
611 | 3373 |  | 36 | 7 |  | 21620.8 |  | multi-Si module |  |  | OE 0 days |  |  |  | #DIV/0! |  | #DIV/0! |  | 6.0926 | 86.3477 | 5.7585 | 0.94515 | 72.8998 | 0.84426 | 419.791 | 79.795 | 25 | back of panel |  | SPIRE | 4600SLP | 3/16/2016 | 14:41 | PSEL | FLI Proline |  |  |  |  | 4.811 | 88.118 | 6.4 | 1.206 | 81.475 | 25.6 | [5 empty] | 3/16/2016 |  | 3/16/2016 |  | PSEL | ./EL/3373_36_7_03162016_80.tiff | ./EL/3373_36_7_03162016_20.tiff | ./IV/3373_36_7_03162016.csv | 0 | 0 | 1 | ./RefIV/3373_36_7_03162016.csv |  |  | 3/16/2016 | 14:32 | #DIV/0! | #DIV/0!
612 | 3366 |  | 36 | 5 |  | 21620.8 |  | multi-Si module |  |  | OE 0 days |  |  |  | #DIV/0! |  | #DIV/0! |  | 6.0304 | 69.5003 | 5.6468 | 0.93639 | 59.2153 | 0.85202 | 334.378 | 79.781 | 25 | back of panel |  | SPIRE | 4600SLP | 3/16/2016 | 10:02 | PSEL | FLI Proline |  |  |  |  | 4.811 | 71.116 | 1.2 | 1.206 | 66.162 | 4.8 | [5 empty] | 3/16/2016 |  | 3/16/2016 |  | PSEL | ./EL/3366_36_5_03162016_80.tiff | ./EL/3366_36_5_03162016_20.tiff | ./IV/3366_36_5_03162016.csv | 0 | 0 | 1 | ./RefIV/3366_36_5_03162016.csv |  |  | 3/16/2016 | 9:57 | #DIV/0! | #DIV/0!
613 | 3375 |  | 36 | 5 |  | 21620.8 |  | multi-Si module |  |  | OE 0 days |  |  |  | #DIV/0! |  | #DIV/0! |  | 6.0314 | 92.6224 | 5.6582 | 0.93811 | 78.7708 | 0.85045 | 445.697 | 79.781 | 25 | back of panel |  | SPIRE | 4600SLP | 3/16/2016 | 16:10 | PSEL | FLI Proline |  |  |  |  | 4.806 | 94.686 | 1.2 | 1.206 | 88.081 | 4.8 | [5 empty] | 3/16/2016 |  | 3/16/2016 |  | PSEL | ./EL/3375_36_5_03162016_80.tiff | ./EL/3375_36_5_03162016_20.tiff | ./IV/3375_36_5_03162016.csv | 0 | 0 | 1 | ./RefIV/3375_36_5_03162016.csv |  |  | 3/16/2016 | 16:07 | #DIV/0! | #DIV/0!
614 | 3354 |  | 36 | 6 |  | 21620.8 |  | multi-Si module |  |  | OE 0 days |  |  |  | #DIV/0! |  | #DIV/0! |  | 6.1598 | 86.2268 | 5.7985 | 0.94134 | 72.6645 | 0.84271 | 421.345 | 79.328 | 25 | back of panel |  | SPIRE | 4600SLP | 3/15/2016 | 14:26 | PSEL | FLI Proline |  |  |  |  | 4.906 | 87.292 | 9.6 | 1.206 | 80.762 | 38.4 | [5 empty] | 3/15/2016 |  | 3/15/2016 |  | PSEL | ./EL/3354_36_6_03152016_80.tiff | ./EL/3354_36_6_03152016_20.tiff | ./IV/3354_36_6_03152016.csv | 0 | 0 | 1 | ./RefIV/3354_36_6_03152016.csv |  |  | 3/15/2016 | 14:26 | #DIV/0! | #DIV/0!
615 | 3358 |  | 36 | 6 |  | 21620.8 |  | multi-Si module |  |  | OE 0 days |  |  |  | #DIV/0! |  | #DIV/0! |  | 6.1736 | 85.6605 | 5.8048 | 0.94026 | 72.0426 | 0.84102 | 418.192 | 79.078 | 25 | back of panel |  | SPIRE | 4600SLP | 3/15/2016 | 16:47 | PSEL | FLI Proline |  |  |  |  | 4.9 | 88.118 | 9.6 | 1.206 | 81.55 | 38.4 | [5 empty] | 3/15/2016 |  | 3/15/2016 |  | PSEL | ./EL/3358_36_6_03152016_80.tiff | ./EL/3358_36_6_03152016_20.tiff | ./IV/3358_36_6_03152016.csv | 0 | 0 | 1 | ./RefIV/3358_36_6_03152016.csv |  |  | 3/15/2016 | 16:47 | #DIV/0! | #DIV/0!

## Sheet1
current | 1.0036
Voltage | 0.99764
| 1.0012 | 0.99371 | 0.9968
|  | 0.99487 | 0.99745
|  | 0.99291 | 0.99188
|  | 0.99976 | 0.99758
|  | 0.99774 | 0.99051
|  | 0.99597 | 0.99551
|  | 0.99959 | 0.99508
|  | 1.0004 | 0.99279
|  | 0.99494 | 0.99382
|  | 1.0003 | 0.99635
|  | 1.0008 | 0.99362
|  | 0.99565 | 0.98688
|  | 0.99633 | 0.99674
|  | 0.994 | 0.99064
|  | 0.99435 | 0.99636
|  | 0.99275 | 0.99155
|  | 0.99836 | 0.99947
|  | 0.99802 | 0.99808
|  | 0.9948 | 0.99272
|  | 0.99644 | 0.99557
|  | 0.99564 | 0.99233
|  | 0.99563 | 0.99951
|  | 0.99473 | 0.99304
|  | 0.99166 | 0.9911
|  | 0.99258 | 0.99142
|  | 0.99619 | 0.98915
|  | 0.99432 | 0.98779
|  | 1.0157 | 0.97813
|  | 1.0173 | 0.97914
|  | 1.0174 | 0.9783
|  | 1.0166 | 0.97745
|  | 1.0184 | 0.97826
|  | 1.0119 | 0.97564
|  | 1.0178 | 0.97824
|  | 1.0174 | 0.97914
|  | 1.0176 | 0.97412
|  | 1 | 1.0035
|  | 0.9966 | 1.0043
|  | 1.0006 | 1.0031
|  | 1.0003 | 1.001
|  | 0.99575 | 0.99868
|  | 1.0026 | 1.0023
|  | 0.99885 | 1.0006
|  | 0.99813 | 0.99961
|  | 0.99813 | 0.99961
|  | 1.0025 | 1.0029
|  | 1.0002 | 1.0015
|  | 1.0006 | 1.0005
|  | 1.0058 | 1.0023
|  | 1.0009 | 0.99907
|  | 1.0014 | 0.99959
|  | 1.0032 | 1.0027
|  | 1.0029 | 1.0026
|  | 0.99903 | 1.002
|  | 1.0029 | 1.0048
|  | 1.006 | 1.0036
|  | 1.0006 | 0.99789
|  | 1.0011 | 1.0004
|  | 1.0016 | 1.0034
|  | 0.99931 | 1.0031
|  | 1.0011 | 1.0037
|  | 1.0018 | 1.0019
|  | 1.002 | 0.99882
|  | 1.0016 | 0.9994
|  | 0.99961 | 1.0038
|  | 1.002 | 1.0041
|  | 1.0028 | 1.0028
|  | 1.002 | 0.99994
|  | 1.001 | 0.99197
|  | 0.99911 | 0.99092
|  | 0.99407 | 0.99334
|  | 1.0028 | 0.99458
|  | 1.0004 | 0.99563
|  | 0.99556 | 0.99869
|  | 1.002 | 0.99135
|  | 0.99987 | 0.99247
|  | 1.001 | 0.99278
|  | 1.0001 | 0.99789
|  | 1.0005 | 0.99574
|  | 1.0007 | 0.99768
|  | 0.99886 | 0.99681
|  | 0.99982 | 0.99401
|  | 1.0039 | 0.99688
|  | 1.013 | 0.98978
|  | 1.014 | 0.99355
|  | 1.0133 | 0.98978
|  | 1.0141 | 0.99082
|  | 1.0154 | 0.98887
|  | 1.0142 | 0.99296
|  | 1.0105 | 0.98826
|  | 1.0121 | 0.98902
|  | 1.0115 | 0.98722
|  | 1.0126 | 0.99102
|  | 1.0138 | 0.98847
|  | 1.0137 | 0.99264
|  | 1.0124 | 0.98962
|  | 1.0122 | 0.9947
|  | 1.0146 | 0.98853
|  | 1.0137 | 0.99173
|  | 1.0129 | 0.99007
|  | 1.0137 | 0.9879
|  | 1.0089 | 0.99222
|  | 1.0084 | 1.003
|  | 1.0079 | 0.99907
|  | 1.0164 | 0.99218
|  | 1.0169 | 0.99869
|  | 1.0153 | 0.99126
|  | 1.0124 | 1
|  | 1.0155 | 0.99025
|  | 1.014 | 0.99025
|  | 1.0167 | 0.99774
|  | 1.0131 | 0.98448
|  | 1.0118 | 0.99308
|  | 1.0095 | 0.98994
|  | 1.0206 | 0.9914
|  | 1.0214 | 0.9961
|  | 1.0142 | 0.99657
|  | 1.0148 | 0.99473
|  | 1.0166 | 1
|  | 1.0143 | 0.99103
|  | 1.0147 | 0.99777
|  | 1.0161 | 0.98772
|  | 1.0173 | 0.9948
|  | 1.01 | 0.99288
|  | 1.0178 | 0.9914
|  | 1.0156 | 0.99565
|  | 1.0115 | 0.99298
|  | 1.0185 | 0.99377
|  | 1.0189 | 0.99969
|  | 1.018 | 0.99592
|  | 1.0021 | 1.0004
|  | 1.0156 | 0.9911
|  | 1.0012 | 1.0013
|  | 1.0026 | 0.99843
|  | 0.99761 | 0.9988
|  | 0.99731 | 0.99815
|  | 1.0006 | 0.99595
|  | 0.99736 | 0.99982
|  | 0.99944 | 0.99718
|  | 0.99683 | 0.9986
|  | 1.0001 | 0.99607
|  | 0.99747 | 0.9991
|  | 0.99912 | 0.99543
|  | 1.0001 | 0.99945
|  | 1.0035 | 0.99697
|  | 0.99582 | 0.99814
|  | 0.99875 | 0.99609
|  | 0.99866 | 0.99999
|  | 0.99941 | 0.99789
|  | 0.99912 | 0.99899
|  | 1.0018 | 0.99646
|  | 1.0085 | 1.0039
|  | 0.99739 | 0.99945
|  | 1.0134 | 1.0042
|  | 1.0036 | 0.99977
|  | 1.0108 | 1.0031
|  | 1.002 | 0.99807
|  | 1.0125 | 1.0032
|  | 1.0008 | 0.99869
|  | 1.012 | 1.0024
|  | 1.0011 | 0.99893
|  | 1.0108 | 1.0012
|  | 1.0004 | 0.99541
|  | 1.0129 | 1.0043
|  | 1.0015 | 1
|  | 1.0109 | 1.0015
|  | 1.0004 | 0.99728
|  | 1.0094 | 1.0055
|  | 0.99341 | 1.0012
|  | 1.0119 | 1.0026
|  | 1.0013 | 0.9977
|  | 1.0124 | 1.0022
|  | 1.0016 | 0.99749
|  | 1.0099 | 1.0019
|  | 0.99858 | 0.99801
|  | 1.013 | 1.0028
|  | 1.0024 | 0.9975
|  | 1.009 | 1.0047
|  | 1.0109 | 1.0022
|  | 1.0106 | 1.0057
|  | 0.99734 | 1.0022
|  | 0.99972 | 0.99812
|  | 0.99725 | 0.99886
|  | 1.0007 | 1.0016
|  | 1.0007 | 0.99898
|  | 1.002 | 0.99884
|  | 1.0026 | 0.99562
|  | 1.0011 | 0.99841
|  | 1.0022 | 0.99384
|  | 1.0019 | 0.99624
|  | 1.0014 | 0.99004
|  | 0.9998 | 1.0003
|  | 0.99796 | 0.99504
|  | 0.99971 | 0.99977
|  | 1.0007 | 0.99475
|  | 1.0017 | 0.99794
|  | 1.0003 | 0.99277
|  | 1.0023 | 1.001
|  | 1.0001 | 0.99591
|  | 1.0002 | 1.0022
|  | 1.0009 | 0.99854
|  | 1.0027 | 0.99713
|  | 1.0028 | 0.99881
|  | 1.0008 | 0.99481
|  | 1.0011 | 0.99655
|  | 1.0002 | 0.99111
|  | 1.0023 | 0.99878
|  | 1.0019 | 0.99722
|  | 1.0031 | 0.99399
|  | 1.0015 | 0.99909
|  | 0.99988 | 0.99892
|  | 0.99965 | 0.99409
|  | 0.99892 | 0.9898
|  | 1.0003 | 0.99729
|  | 1.0007 | 0.99285
|  | 1.0013 | 0.99895
|  | 1.0008 | 0.99407
|  | 1.0028 | 0.99924
|  | 1.0008 | 0.99017
|  | 1.002 | 0.99742
|  | 1.0028 | 0.99195
|  | 1.004 | 0.99898
|  | 1.0014 | 0.98998
|  | 1.0033 | 0.99907
|  | 1.0029 | 0.99363
|  | 1.0045 | 0.99949
|  | 1.0033 | 0.99448
|  | 1.0016 | 1.0008
|  | 0.99807 | 0.99274
|  | 0.99874 | 0.99689
|  | 1.0024 | 0.99898
|  | 1.0024 | 0.9933
|  | 0.99829 | 0.98966
|  | 1.0063 | 0.99536
|  | 1.0061 | 0.99507
|  | 1.0094 | 0.99759
|  | 1.0085 | 0.99792
|  | 1.0087 | 0.99645
|  | 1.0055 | 0.99614
|  | 1.0051 | 0.99693
|  | 1.0068 | 0.99775
|  | 1.0078 | 0.99835
|  | 1.0049 | 0.9955
|  | 1.0116 | 0.98586
|  | 1.0114 | 0.98307
|  | 1.012 | 0.98775
|  | 1.0079 | 0.99612
|  | 1.0057 | 0.99162
|  | 1.0061 | 0.99589
|  | 1.0113 | 0.98358
|  | 1.0108 | 0.98111
|  | 1.012 | 0.98573
|  | 1.0082 | 0.99952
|  | 1.0091 | 0.99243
|  | 1.0094 | 0.99786
|  | 1.0115 | 1.002
|  | 1.0097 | 0.9957
|  | 1.0111 | 1.0045
|  | 1.0112 | 1.0023
|  | 1.0101 | 0.99778
|  | 1.0114 | 1.0049
|  | 1.0098 | 0.97796
|  | 1.0117 | 0.98313
|  | 1.0111 | 0.9788
|  | 1.0099 | 0.98084
|  | 1.0119 | 0.98402
|  | 1.0076 | 0.9759
|  | 1.0098 | 0.98058
|  | 1.0103 | 0.97677
|  | 1.0074 | 0.97688
|  | 1.0009 | 0.98269
|  | 1.0096 | 0.97799
|  | 1.0104 | 0.98212
|  | 1.0118 | 0.98153
|  | 1.013 | 0.98599
|  | 1.0106 | 0.97798
|  | 1.0116 | 0.98059
|  | 1.0127 | 0.98434
|  | 1.0099 | 0.979
|  | 1.0111 | 0.98339
|  | 1.0043 | 0.98988
|  | 1.0044 | 0.99567
|  | 1.0086 | 0.99241
|  | 1.0089 | 0.99651
|  | 1.0065 | 0.99292
|  | 1.0042 | 0.98949
|  | 1.0052 | 0.99545
|  | 1.0056 | 0.98911
|  | 1.0064 | 0.99545
|  | 1.0018 | 0.99175
|  | 1.0021 | 0.99684
|  | 1.0089 | 0.98924
|  | 1.0099 | 0.99596
|  | 1.0023 | 0.99067
|  | 1.0034 | 0.99637
|  | 1.0035 | 0.98943
|  | 1.0074 | 0.98867
|  | 1.0074 | 0.99458
|  | 1.0016 | 0.9905
|  | 1.0021 | 0.99604
|  | 1.006 | 0.98949
|  | 1.0065 | 0.99354
|  | 1.0062 | 0.98724
|  | 1.0024 | 0.99625
|  | 1.0108 | 0.98383
|  | 1.0067 | 0.9946
|  | 1.0102 | 0.98453
|  | 0.99497 | 1.0008
|  | 0.99445 | 1.0077
|  | 0.99287 | 1.0033
|  | 0.99438 | 1.0044
|  | 0.99646 | 1.0037
|  | 0.99684 | 1.0077
|  | 0.9929 | 1.0046
|  | 0.99373 | 1.0076
|  | 0.99648 | 1.0042
|  | 0.99474 | 1.0038
|  | 0.99471 | 1.0061
|  | 0.99441 | 1.0065
|  | 0.99396 | 1.0018
|  | 0.99492 | 1.0096
|  | 0.9958 | 1.0064
|  | 0.9946 | 1.0064
|  | 0.99605 | 1.0043
|  | 0.99565 | 1.0043
|  | 0.99739 | 1.0058
|  | 0.9964 | 1.0068
|  | 0.99395 | 1.0028
|  | 0.99518 | 1.0062
|  | 0.99548 | 1.007
|  | 0.99586 | 1.0067
|  | 0.99421 | 1.004
|  | 0.9958 | 1.005
|  | 0.99447 | 1.0116
|  | 0.9949 | 1.0126
|  | 0.99503 | 1.0115
|  | 0.99376 | 1.0049
|  | 0.99579 | 1.0126
|  | 0.99566 | 1.0106
|  | 0.9934 | 1.011
|  | 0.99647 | 1.0081
|  | 0.99171 | 1.0121
|  | 0.99544 | 1.0105
|  | 0.99483 | 1.0033
|  | 0.99589 | 1.0123
|  | 0.99473 | 1.0064
|  | 0.99746 | 1.0111
|  | 0.99381 | 1.0128
|  | 0.9956 | 1.0117
|  | 0.99543 | 1.0111
|  | 0.99428 | 1.0088
|  | 0.99576 | 1.0108
|  | 0.99691 | 1.0129
|  | 0.99566 | 1.0127
|  | 0.99637 | 1.0075
|  | 0.99473 | 1.0113
|  | 0.99546 | 1.0125
|  | 0.99584 | 1.0062
|  | 0.99482 | 1.0102
|  | 0.99715 | 1.0135
|  | 0.99732 | 1.0049
|  | 0.99383 | 1.0085
|  | 0.99404 | 1.0119
|  | 0.99433 | 1.0061
|  | 0.99438 | 1.0135
|  | 0.9969 | 1.0118
|  | 0.99519 | 1.0055
|  | 0.99475 | 1.0098
|  | 0.99422 | 1.0028
|  | 0.99589 | 1.0115
|  | 0.99438 | 1.0036
|  | 0.99658 | 1.0108
|  | 0.99489 | 1.0111
|  | 0.99761 | 1.0123
|  | 0.99448 | 1.0111
|  | 0.99487 | 1.0061
|  | 0.99469 | 1.0129
|  | 0.99502 | 1.0138
|  | 0.99526 | 1.0119
|  | 0.99418 | 1.0078
|  | 0.99534 | 1.0139
|  | 0.9942 | 1.0149
|  | 0.99505 | 1.014
|  | 0.99668 | 1.0137
|  | 0.99381 | 1.0107
|  | 0.99463 | 1.0071
|  | 0.99589 | 1.0119
|  | 0.99368 | 1.0124
|  | 0.99411 | 1.0124
|  | 0.99545 | 1.0115
|  | 0.99563 | 1.0102
|  | 0.9954 | 1.0103
|  | 1.0039 | 0.97311
|  | 1.0029 | 0.97325
|  | 0.99878 | 0.97217
|  | 1.0017 | 0.96888
|  | 1.0003 | 0.97432
|  | 1.0042 | 0.972
|  | 0.99858 | 0.97437
|  | 1.0002 | 0.97254
|  | 1.0006 | 0.96764
|  | 0.99797 | 0.97215
|  | 1.002 | 0.97267
|  | 1.0019 | 0.97313
|  | 0.99765 | 0.97179
|  | 1.0029 | 0.97392
|  | 1.0011 | 0.97377
|  | 1.0011 | 0.97365
|  | 1.0084 | 1.0025
|  | 1.0083 | 1.0044
|  | 1.011 | 1.0006
|  | 1.005 | 0.9997
|  | 1.0057 | 1.001
|  | 1.0095 | 1.0012
|  | 1.0096 | 1.0033
|  | 1.0094 | 1.0006
|  | 1.011 | 1.0034
|  | 1.0077 | 1.0007
|  | 1.0107 | 1.003
|  | 1.0111 | 1.0013
|  | 1.0111 | 1.0034
|  | 1.0085 | 1.0017
|  | 1.0084 | 1.0035
|  | 1.0077 | 1.0014
|  | 1.0089 | 1.0036
|  | 1.0066 | 1.0009
|  | 1.0077 | 1.0031
|  | 1.0113 | 1.003
|  | 1.01 | 1.0002
|  | 1.0102 | 1.003
|  | 1.0084 | 1.001
|  | 1.0101 | 1.0044
|  | 1.0107 | 1.003
|  | 1.0118 | 1.0051
|  | 1.0083 | 1.002
|  | 1.0077 | 0.99705
|  | 1.0096 | 1.001
|  | 1.0082 | 0.99387
|  | 1.0078 | 1.0014
|  | 1.0078 | 0.99821
|  | 1.0112 | 1.0033
|  | 1.0107 | 0.9999
|  | 1.0101 | 1.0019
|  | 1.0086 | 0.99662
|  | 1.0103 | 1.0023
|  | 1.0086 | 0.99747
|  | 1.0104 | 1.0022
|  | 1.0069 | 1.0009
|  | 1.0073 | 0.99532
|  | 1.0123 | 1.0037
|  | 1.0113 | 1.0005
|  | 1.0074 | 1.0025
|  | 1.0072 | 0.99882
|  | 1.0103 | 1.0023
|  | 1.0113 | 1.0048
|  | 1.01 | 1.004
|  | 0.98068 | 0.98715
|  | 0.98635 | 0.98676
|  | 0.98364 | 0.98741
|  | 0.98459 | 0.9876
|  | 0.98406 | 0.98885
|  | 0.98392 | 0.9878
|  | 0.98511 | 0.98792
|  | 0.98007 | 0.98741
|  | 0.98666 | 0.98942
|  | 0.98257 | 0.98754
|  | 0.98562 | 1.0104
|  | 0.98565 | 1.0039
|  | 0.98313 | 1.0016
|  | 0.98636 | 1.0096
|  | 0.98817 | 1.0073
|  | 0.98706 | 1.002
|  | 0.9846 | 1.0041
|  | 0.98675 | 1.0057
|  | 0.98513 | 1.0048
|  | 0.98505 | 1.0023
|  | 0.98499 | 1.0007
|  | 0.98547 | 1.0074
|  | 0.98649 | 1.0056
|  | 0.98428 | 1.0002
|  | 0.98805 | 1.0036
|  | 0.98609 | 1.0069
|  | 0.98709 | 1.0101
|  | 0.98778 | 1.0025
|  | 0.98553 | 1.0092
|  | 0.98647 | 1.0014
|  | 0.98698 | 1.0023
|  | 0.98698 | 1.0023
|  | 0.98541 | 1.0021
|  | 0.9849 | 1.0054
|  | 0.9856 | 1.0063
|  | 0.98688 | 1.0063
|  | 1.017 | 0.98625
|  | 1.0155 | 0.9847
|  | 1.0183 | 0.98914
|  | 1.0177 | 0.98747
|  | 1.0153 | 0.99075
|  | 1.0167 | 0.98978
|  | 1.0162 | 0.98587
|  | 1.0166 | 0.98841
|  | 1.0167 | 0.98409
|  | 1.0155 | 0.98766
|  | 1.0107 | 0.99767
|  | 1.0115 | 1.0014
|  | 1.0104 | 0.99909
|  | 1.0096 | 0.99168
|  | 1.0103 | 1.0007
|  | 1.0105 | 0.9964
|  | 1.011 | 1.003
|  | 1.0078 | 0.99363
|  | 1.0101 | 1.0012
|  | 1.0089 | 0.99135
|  | 1.0098 | 1.0028
|  | 1.0083 | 0.9922
|  | 1.0099 | 0.99937
|  | 1.0108 | 0.98986
|  | 1.0123 | 1.0003
|  | 1.0099 | 0.99421
|  | 1.0098 | 1.0013
|  | 1.0077 | 0.99354
|  | 1.0078 | 0.99606
|  | 1.0079 | 0.99371
|  | 1.0099 | 0.99394
|  | 1.0114 | 0.99911
|  | 1.0121 | 0.99272
|  | 1.0143 | 1.0018
|  | 1.0086 | 0.99207
|  | 1.0108 | 1.0013
|  | 1.0105 | 0.99578
|  | 1.0077 | 1.009
|  | 1.0076 | 1.009
|  | 1.0033 | 1.0005
|  | 1.0027 | 1.0023
|  | 1.0078 | 0.99729
|  | 1.0076 | 0.99983
|  | 1.0089 | 1.0037
|  | 1.0033 | 0.99511
|  | 1.0027 | 0.99589
|  | 1.0021 | 0.99391
|  | 1.0092 | 0.99828
|  | 1.0084 | 0.99877
|  | 1.0075 | 0.99684
|  | 1.0101 | 1.0074
|  | 1.0083 | 1.0025
|  | 1.0075 | 1.0038
|  | 1.005 | 1.0019
|  | 1.0082 | 1.0029
|  | 1.0071 | 1.0032
|  | 1.0104 | 1.0088
|  | 1.0105 | 1.009
|  | 1.0077 | 1.0041
|  | 1.0073 | 1.0045
|  | 1.0098 | 1.0072
|  | 1.0095 | 1.008
|  | 1.0098 | 1.009
|  | 1.0089 | 1.0095
|  | 1.0086 | 1.0023
|  | 1.0075 | 1.003
|  | 1.0124 | 1.0093
|  | 1.0118 | 1.0103
|  | 1.0128 | 1.0039
|  | 1.0046 | 1.0024
|  | 1.0136 | 1.0016
|  | 1.0103 | 1.0101
|  | 0.9974 | 0.99158
|  | 0.99261 | 0.98967
|  | 0.99299 | 0.98947
|  | 0.98989 | 0.98506
|  | 0.99873 | 0.98853
|  | 0.99937 | 0.99093
|  | 0.99456 | 0.98765
|  | 1.0041 | 0.98918
|  | 0.99986 | 0.99267
|  | 0.99867 | 1.0034
|  | 1.0052 | 0.97305
|  | 1.0071 | 0.9773
|  | 1.0057 | 0.97773
|  | 1.0125 | 0.976
|  | 1.0089 | 0.97862
|  | 1.0067 | 0.97358
|  | 1.0109 | 0.97416
|  | 1.0061 | 0.97864
|  | 1.0053 | 0.9801
|  | 1.0129 | 1.0021
|  | 1.0165 | 1.0191
|  | 1.0111 | 1.0241
|  | 1.0111 | 1.0241
|  | 1.0206 | 1.0162
|  | 1.0185 | 1.0181
|  | 1.0218 | 1.0222
|  | 1.0152 | 1.0187
|  | 1.0288 | 1.011
|  | 1.0219 | 1.0124
|  | 1.0281 | 1.0182
|  | 1.0256 | 1.018
|  | 1.021 | 1.0239
|  | 1.0217 | 1.0259
|  | 1.0297 | 1.0094